## Sheet3 (hidden)
# | Project | Present Value
|  | Updated | Original | Delta
1 | Alberhill System Project | 449.1135 | 467.28 | 3.888%
2 | Tie to SDG&E | 383.0032 | 359.15 | -6.642%
3 | Tie between VS and VN+VS+EC | 455.5076 | 378.59 | -20.32%
4 | ES at Pechanga | 604.8153 | 216.52 | -179.3%
5 | ES at Pechanga + Mira Loma Tap | 605.2969 | 454.67 | -33.13%

## Summary
Summary of Cost-Benefit analysis
($ millions)
# | Project | Total Nominal Capital Cost | Present Value of Revenue Requirement | Benefit($M) | Benefit-Cost Ratio | # | Project | Cost-Benefit Ratio
1 | Alberhill System Project | 545 | 545 | 9838.7312 | 18.0527 | 1 | Alberhill System Project | 0.055393
2 | SDG&E | 540 | 469 | 4596.8658 | 9.8014 | 13 | Valley South to Valley North | 0.056567
3 | Valley South to Valley North to Vista | 285 | 270 | 3465.6256 | 12.8357 | 6 | Valley South to Valley North and Distributed BESS in Valley South | 0.058706
4 | Centralized BESS in Valley South | 2363 | 923 | 3422.0829 | 3.7076 | 8 | Mira Loma | 0.06075
5 | Mira Loma and Centralized BESS in Valley South | 2156 | 829 | 6931.7817 | 8.3616 | 3 | Valley South to Valley North to Vista | 0.077908
6 | Valley South to Valley North and Distributed BESS in Valley South | 324 | 213 | 3628.2395 | 17.034 | 7 | Menifee | 0.081945
7 | Menifee | 358 | 315 | 3844.0314 | 12.2033 | 9 | SCE Orange County | 0.097517
8 | Mira Loma | 328 | 290 | 4773.6635 | 16.4609 | 2 | SDG&E | 0.10203
9 | SCE Orange County | 951 | 806 | 8265.2328 | 10.2546 | 11 | Valley South to Valley North to Vista and Centralized BESS in Valley South | 0.10062
10 | Valley South to Valley North and Centralized BESS in Valley South and Valley North | 2582 | 726 | 4113.5639 | 5.6661 | 5 | Mira Loma and Centralized BESS in Valley South | 0.11959
11 | Valley South to Valley North to Vista and Centralized BESS in Valley South | 951 | 400 | 3975.3943 | 9.9385 | 12 | SDG&E and Centralized BESS in Valley South | 0.14044
12 | SDG&E and Centralized BESS in Valley South | 1473 | 701 | 4991.5798 | 7.1207 | 10 | Valley South to Valley North and Centralized BESS in Valley South and Valley North | 0.17649
13 | Valley South to Valley North | 190 | 185 | 3270.4391 | 17.678 | 4 | Centralized BESS in Valley South | 0.26972
Note on A3: In this spreadsheet all relevant benefits associated with project savings have been monetized and alternatives are ranked using their Cost-to-Benefit ratio performance.

## Incr. C-B Reliability Indices
Incremental Cost-Benefit analysis taking into consideration Non-Monetized Benefits of reliability indices.
# | Project | Present Value | Aggregate | [25 empty] | For Calculations only
0 | Baseline | 0 | 0 | [25 empty] | Category |  |  |  | NPV of benefits between Project and Baseline | NPV of Project Performance
13 | Valley South to Valley North | 185 | 190 | [25 empty] | N-1 | EENS | 1 | N-1 EENS 1 | 8935.2425 | 718.3509
6 | Valley South to Valley North and Distributed BESS in Valley South | 213 | 324 | [25 empty] | N-1 | IP | 1 | N-1 IP 1 | 207.8798 | 58.0604
3 | Valley South to Valley North to Vista | 270 | 285 | [25 empty] | N-1 | SAIDI | 1 | N-1 SAIDI 1 | 1075.3499 | 62.2964
8 | Mira Loma | 290 | 328 | [25 empty] | N-1 | SAIFI | 1 | N-1 SAIFI 1 | 6.6926 | 1.8156
7 | Menifee | 315 | 358 | [25 empty] | N-1 | PFD | 1 | N-1 PFD 1 | 678.7835 | 24.86
11 | Valley South to Valley North to Vista and Centralized BESS in Valley South | 400 | 951 | [25 empty] | N-1 | Available Flex-1 | 1 | N-1 Available Flex-1 1 | 299240.6375 | 0
2 | SDG&E | 469 | 540 | [25 empty] | N-1 | Available Flex-2-1 | 1 | N-1 Available Flex-2-1 1 | 1862863.7959 | 122278.159
1 | Alberhill System Project | 545 | 545 | [25 empty] | N-1 | Available Flex-2-2 | 1 | N-1 Available Flex-2-2 1 | 971617.2786 | 460.9064
12 | SDG&E and Centralized BESS in Valley South | 701 | 1473 | [25 empty] | N-0 | EENS | 1 | N-0 EENS 1 | 21149.4476 | 34.36
10 | Valley South to Valley North and Centralized BESS in Valley South and Valley North | 726 | 2582 | [25 empty] | N-0 | IP | 1 | N-0 IP 1 | 1327.9868 | 7.7156
9 | SCE Orange County | 806 | 951 | [25 empty] | N-0 | SAIDI | 1 | N-0 SAIDI 1 | 1755.4513 | 1.3611
5 | Mira Loma and Centralized BESS in Valley South | 829 | 2156 | [25 empty] | N-0 | SAIFI | 1 | N-0 SAIFI 1 | 22.4262 | 0.1191
4 | Centralized BESS in Valley South | 923 | 2363 | [25 empty] | N-0 | PFD | 1 | N-0 PFD 1 | 278.5405 | 5.8328
[29 empty] | N-1 | EENS | 2 | N-1 EENS 2 | 9597.8795 | 55.714
[29 empty] | N-1 | IP | 2 | N-1 IP 2 | 259.4767 | 6.4635
Present Value of Benefits by Project | [28 empty] | N-1 | SAIDI | 2 | N-1 SAIDI 2 | 1136.4404 | 1.2059
|  | Alberhill System Project | SDG&E | Valley South to Valley North to Vista | Centralized BESS in Valley South | Mira Loma and Centralized BESS in Valley South | Valley South to Valley North and Distributed BESS in Valley South | Menifee | Mira Loma | SCE Orange County | Valley South to Valley North and Centralized BESS in Valley South and Valley North | Valley South to Valley North to Vista and Centralized BESS in Valley South | SDG&E and Centralized BESS in Valley South | Valley South to Valley North | [14 empty] | N-1 | SAIFI | 2 | N-1 SAIFI 2 | 8.4508 | 0.057458
Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | [14 empty] | N-1 | PFD | 2 | N-1 PFD 2 | 700.5517 | 3.0918
N-1 | EENS | 8935.2425 | 9597.8795 | 1471.0441 | 9646.2651 | 8472.3643 | 2641.0479 | 1889.9754 | 2643.0908 | 7597.9801 | 3417.8021 | 3417.8021 | 9653.5934 | 1471.0441 | [14 empty] | N-1 | Available Flex-1 | 2 | N-1 Available Flex-1 2 | 122295.4802 | 176945.1573
N-1 | IP | 207.8798 | 259.4767 | -32.719 | 264.2033 | 133.6977 | -52.4992 | -46.1734 | 27.8523 | 144.9144 | -54.568 | -54.568 | 265.9402 | -32.719 | [14 empty] | N-1 | Available Flex-2-1 | 2 | N-1 Available Flex-2-1 2 | 1302863.5904 | 682278.3646
N-1 | SAIDI | 1075.3499 | 1136.4404 | 374.1303 | 1137.4733 | 1082.0563 | 486.0227 | 606.4801 | 623.6015 | 1059.0133 | 635.0181 | 635.0181 | 1137.6463 | 374.1303 | [14 empty] | N-1 | Available Flex-2-2 | 2 | N-1 Available Flex-2-2 2 | 691817.7936 | 280260.3914
N-1 | SAIFI | 6.6926 | 8.4508 | 0.84873 | 8.4905 | 7.2857 | 1.9948 | 2.1362 | 1.9533 | 6.1176 | 2.697 | 2.697 | 8.5082 | 0.84873 | [14 empty] | N-0 | EENS | 2 | N-0 EENS 2 | 20285.7425 | 898.0651
N-1 | PFD | 678.7835 | 700.5517 | 364.9905 | 702.6918 | 494.9928 | 367.8665 | 388.6179 | 444.5369 | 617.1566 | 387.0171 | 387.0171 | 703.6435 | 364.9905 | [14 empty] | N-0 | IP | 2 | N-0 IP 2 | 1180.6909 | 155.0115
N-1 | Available Flex-1 | 299240.6375 | 122295.4802 | 98755.5743 | 97603.9451 | 213597.0269 | 108576.8331 | 97911.486 | 143555.8795 | 252249.9385 | 112489.2183 | 112489.2183 | 133288.857 | 98755.5743 | [14 empty] | N-0 | SAIDI | 2 | N-0 SAIDI 2 | 1743.4027 | 13.4098
N-1 | Available Flex-2-1 | 1862863.7959 | 1302863.5904 | 0 | 0 | 512526.5558 | 0 | 1159523.3929 | 512526.5558 | 1329505.5441 | 0 | 0 | 1302863.5904 | 0 | [14 empty] | N-0 | SAIFI | 2 | N-0 SAIFI 2 | 21.7647 | 0.78057
N-1 | Available Flex-2-2 | 971617.2786 | 691817.7936 | 625479.561 | 20162.1209 | 587736.118 | 628140.4285 | 625479.561 | 587117.8253 | 735410.3655 | 625479.561 | 625479.561 | 691943.5847 | 625479.561 | [14 empty] | N-0 | PFD | 2 | N-0 PFD 2 | 265.5136 | 18.8597
N-0 | EENS | 21149.4476 | 20285.7425 | 16261.7414 | 21183.8076 | 21183.8076 | 10787.9436 | 20662.7139 | 14173.305 | 20371.8447 | 21183.8076 | 16790.5818 | 21183.8076 | 10376.9204 | [14 empty] | N-1 | EENS | 3 | N-1 EENS 3 | 1471.0441 | 8182.5493
N-0 | IP | 1327.9868 | 1180.6909 | 1010.1631 | 1335.7024 | 1335.7024 | 903.2213 | 1237.886 | 727.3796 | 1184.7372 | 1335.7024 | 1114.1124 | 1335.7024 | 839.4895 | [14 empty] | N-1 | IP | 3 | N-1 IP 3 | -32.719 | 298.6592
N-0 | SAIDI | 1755.4513 | 1743.4027 | 1459.115 | 1756.8124 | 1756.8124 | 610.7 | 1743.7602 | 1505.3441 | 1742.0508 | 1756.8124 | 1469.8767 | 1756.8124 | 601.4071 | [14 empty] | N-1 | SAIDI | 3 | N-1 SAIDI 3 | 374.1303 | 763.516
N-0 | SAIFI | 22.4262 | 21.7647 | 18.1498 | 22.5453 | 22.5453 | 10.892 | 21.9701 | 16.9262 | 21.6476 | 22.5453 | 18.6232 | 22.5453 | 10.5431 | [14 empty] | N-1 | SAIFI | 3 | N-1 SAIFI 3 | 0.84873 | 7.6595
N-0 | PFD | 278.5405 | 265.5136 | 199.6331 | 284.3733 | 284.3733 | 126.5246 | 273.7617 | 163.2642 | 267.1157 | 284.3733 | 212.762 | 284.3733 | 121.8543 | [14 empty] | N-1 | PFD | 3 | N-1 PFD 3 | 364.9905 | 338.653
[29 empty] | N-1 | Available Flex-1 | 3 | N-1 Available Flex-1 3 | 98755.5743 | 200485.0632
Ranking of Projects by Cost | [28 empty] | N-1 | Available Flex-2-1 | 3 | N-1 Available Flex-2-1 3 | 0 | 1985141.9549
[29 empty] | N-1 | Available Flex-2-2 | 3 | N-1 Available Flex-2-2 3 | 625479.561 | 346598.624
Category |  | 0 | 13 | 6 | 3 | 8 | 7 | 11 | 2 | 1 | 12 | 10 | 9 | 5 | 4 | [13 empty] | N-0 | EENS | 3 | N-0 EENS 3 | 16261.7414 | 4832.5484
[29 empty] | N-0 | IP | 3 | N-0 IP 3 | 1010.1631 | 325.5393
[29 empty] | N-0 | SAIDI | 3 | N-0 SAIDI 3 | 1459.115 | 297.6974
Category |  | 1: Alternative selection | [13 empty] | Preferred Trend | N-0 | SAIFI | 3 | N-0 SAIFI 3 | 18.1498 | 4.3954
|  | 1: 0 --> 13; 3: 13 --> 6; 5: 6 --> 3; 7: 6 --> 8; 9: 8 --> 7; 11: 8 --> 11; 13: 8 --> 2 |  | 8 --> 1 |  | 1 --> 12 |  | 1 --> 10 |  | 1 --> 9 |  | 1 --> 5 |  | 1 --> 4 |  |  | N-0 | PFD | 3 | N-0 PFD 3 | 199.6331 | 84.7402
|  | 0 | 13 | 13 | 6 | 6 | 3 | 6 | 8 | 8 | 7 | 8 | 11 | 8 | 2 | 8 | 1 | 1 | 12 | 1 | 10 | 1 | 9 | 1 | 5 | 1 | 4 |  | N-1 | EENS | 4 | N-1 EENS 4 | 9646.2651 | 7.3283
N-1 | EENS | 1: -7.9516; 3: -41.7858; 5: 20.5264; 7: -0.026532; 9: 30.1246; 11: -7.0428; 13: -38.8536 |  | -24.6751 |  | -4.6048 |  | 30.4831 |  | 5.1236 |  | 1.6299 |  | -1.881 |  | ↓ | N-1 | IP | 4 | N-1 IP 4 | 264.2033 | 1.7369
N-1 | IP | 1: 0.17686; 3: 0.70643; 5: -0.34702; 7: -1.0435; 9: 2.961; 11: 0.74928; 13: -1.294 |  | -0.70599 |  | -0.37218 |  | 1.45 |  | 0.24125 |  | 0.2612 |  | -0.149 |  | ↓ | N-1 | SAIDI | 4 | N-1 SAIDI 4 | 1137.4733 | 0.17294
N-1 | SAIDI | 1: -2.0223; 3: -3.9962; 5: 1.963; 7: -1.7867; 9: 0.68486; 11: -0.10379; 13: -2.865 |  | -1.7716 |  | -0.39934 |  | 2.4328 |  | 0.062592 |  | -0.023614 |  | -0.16435 |  | ↓ | N-1 | SAIFI | 4 | N-1 SAIFI 4 | 8.4905 | 0.017671
N-1 | SAIFI | 1: -0.0045877; 3: -0.04093; 5: 0.020106; 7: 0.00053909; 9: -0.0073177; 11: -0.0067618; 13: -0.036299 |  | -0.018586 |  | -0.011638 |  | 0.022075 |  | 0.0022032 |  | -0.0020882 |  | -0.0047564 |  | ↓ | N-1 | PFD | 4 | N-1 PFD 4 | 702.6918 | 0.95173
N-1 | PFD | 1: -1.9729; 3: -0.10271; 5: 0.050456; 7: -0.99572; 9: 2.2368; 11: 0.52291; 13: -1.4303 |  | -0.91861 |  | -0.15936 |  | 1.612 |  | 0.23612 |  | 0.64715 |  | -0.063249 |  | ↓ | N-1 | Available Flex-1 | 4 | N-1 Available Flex-1 4 | 97603.9451 | 201636.6924
N-1 | Available Flex-1 | 1: -533.8139; 3: -350.7592; 5: 172.3028; 7: -454.2733; 9: 1825.7757; 11: 282.4242; 13: 118.7732 |  | -610.5285 |  | 1063.7935 |  | 1031.7758 |  | 180.041 |  | 301.562 |  | 533.4304 |  | ↓ | N-1 | Available Flex-2-1 | 4 | N-1 Available Flex-2-1 4 | 0 | 1985141.9549
N-1 | Available Flex-2-1 | 1: 0; 3: 0; 5: 0; 7: -6656.189; 9: -25879.8735; 11: 4659.3323; 13: -4415.2907 |  | -5295.4402 |  | 3589.7449 |  | 10292.0652 |  | 2043.5182 |  | 4754.7086 |  | 4928.2111 |  | ↓ | N-1 | Available Flex-2-2 | 4 | N-1 Available Flex-2-2 4 | 20162.1209 | 951916.0641
N-1 | Available Flex-2-2 | 1: -3380.9706; 3: -95.031; 5: 46.6819; 7: 532.7611; 9: -1534.4694; 11: -348.7431; 13: -584.916 |  | -1507.841 |  | 1792.7801 |  | 1912.3631 |  | 905.0073 |  | 1351.6942 |  | 2517.0771 |  | ↓ | N-0 | EENS | 4 | N-0 EENS 4 | 21183.8076 | 0
N-0 | EENS | 1: -58.9501; 3: 0; 5: -95.5351; 7: -62.5548; 9: -197.6094; 11: -9.71; 13: -25.4931 |  | -21.2822 |  | -0.22026 |  | -0.18983 |  | 2.9793 |  | -0.12099 |  | -0.090899 |  | ↓ | N-0 | IP | 4 | N-0 IP 4 | 1335.7024 | 0
N-0 | IP | 1: -4.5378; 3: -2.2761; 5: -1.8762; 7: 1.963; 9: -19.4326; 11: -3.2913; 13: -2.3945 |  | -2.2585 |  | -0.049459 |  | -0.042628 |  | 0.54885 |  | -0.027168 |  | -0.020412 |  | ↓ | N-0 | SAIDI | 4 | N-0 SAIDI 4 | 1756.8124 | 0
N-0 | SAIDI | 1: -3.2508; 3: -0.33189; 5: -14.8845; 7: -11.652; 9: -9.4342; 11: 0.34572; 13: -1.3156 |  | -0.97076 |  | -0.0087251 |  | -0.00752 |  | 0.051343 |  | -0.0047927 |  | -0.0036008 |  | ↓ | N-0 | SAIFI | 4 | N-0 SAIFI 4 | 22.5453 | 0
N-0 | SAIFI | 1: -0.05699; 3: -0.012459; 5: -0.12733; 7: -0.080875; 9: -0.19403; 11: -0.013672; 13: -0.025952 |  | -0.020811 |  | -0.00076346 |  | -0.00065801 |  | 0.0029831 |  | -0.00041936 |  | -0.00031508 |  | ↓ | N-0 | PFD | 4 | N-0 PFD 4 | 284.3733 | 0
N-0 | PFD | 1: -0.65867; 3: -0.16679; 5: -1.2826; 7: -0.85039; 9: -3.2703; 11: -0.18871; 13: -0.41067 |  | -0.33936 |  | -0.03739 |  | -0.032225 |  | 0.043773 |  | -0.020538 |  | -0.015431 |  | ↓ | N-1 | EENS | 5 | N-1 EENS 5 | 8472.3643 | 1181.2291
Decision to move forward (Y/N) | [15 empty] | Y |  | N |  | N |  | N |  | N |  | N |  |  | N-1 | IP | 5 | N-1 IP 5 | 133.6977 | 132.2426 | bar: 1; 3; 5; 7; 9; 11; 13
[29 empty] | N-1 | SAIDI | 5 | N-1 SAIDI 5 | 1082.0563 | 55.5899
[29 empty] | N-1 | SAIFI | 5 | N-1 SAIFI 5 | 7.2857 | 1.2225
Category |  | 1: Baseline - Alberhill | [14 empty] | N-1 | PFD | 5 | N-1 PFD 5 | 494.9928 | 208.6507
|  | 1: 0 --> 12 | [14 empty] | N-1 | Available Flex-1 | 5 | N-1 Available Flex-1 5 | 213597.0269 | 85643.6106
|  | 1: 0; 2: 12 | [14 empty] | N-1 | Available Flex-2-1 | 5 | N-1 Available Flex-2-1 5 | 512526.5558 | 1472615.3991
N-1 | EENS | 1: -13.7712 | [14 empty] | N-1 | Available Flex-2-2 | 5 | N-1 Available Flex-2-2 5 | 587736.118 | 384342.067
N-1 | IP | 1: -0.37937 | [14 empty] | N-0 | EENS | 5 | N-0 EENS 5 | 21183.8076 | 0
N-1 | SAIDI | 1: -1.6229 | [14 empty] | N-0 | IP | 5 | N-0 IP 5 | 1335.7024 | 0
N-1 | SAIFI | 1: -0.012137 | [14 empty] | N-0 | SAIDI | 5 | N-0 SAIDI 5 | 1756.8124 | 0
N-1 | PFD | 1: -1.0038 | [14 empty] | N-0 | SAIFI | 5 | N-0 SAIFI 5 | 22.5453 | 0
N-1 | Available Flex-1 | 1: -190.141 | [14 empty] | N-0 | PFD | 5 | N-0 PFD 5 | 284.3733 | 0
N-1 | Available Flex-2-1 | 1: -1858.5786 | [14 empty] | N-1 | EENS | 0 | N-1 EENS 0 | 0 | 9653.5934
N-1 | Available Flex-2-2 | 1: -987.0807 | [14 empty] | N-1 | IP | 0 | N-1 IP 0 | 0 | 265.9402
N-0 | EENS | 1: -30.2194 | [14 empty] | N-1 | SAIDI | 0 | N-1 SAIDI 0 | 0 | 1137.6463
N-0 | IP | 1: -1.9054 | [14 empty] | N-1 | SAIFI | 0 | N-1 SAIFI 0 | 0 | 8.5082
N-0 | SAIDI | 1: -2.5062 | [14 empty] | N-1 | PFD | 0 | N-1 PFD 0 | 0 | 703.6435
N-0 | SAIFI | 1: -0.032162 | [14 empty] | N-1 | Available Flex-1 | 0 | N-1 Available Flex-1 0 | 0 | 299240.6375
N-0 | PFD | 1: -0.40567 | [14 empty] | N-1 | Available Flex-2-1 | 0 | N-1 Available Flex-2-1 0 | 0 | 1985141.9549
[29 empty] | N-1 | Available Flex-2-2 | 0 | N-1 Available Flex-2-2 0 | 0 | 972078.185
[29 empty] | N-0 | EENS | 0 | N-0 EENS 0 | 0 | 21183.8076
[29 empty] | N-0 | IP | 0 | N-0 IP 0 | 0 | 1335.7024
[29 empty] | N-0 | SAIDI | 0 | N-0 SAIDI 0 | 0 | 1756.8124
[29 empty] | N-0 | SAIFI | 0 | N-0 SAIFI 0 | 0 | 22.5453
[29 empty] | N-0 | PFD | 0 | N-0 PFD 0 | 0 | 284.3733
[29 empty] | N-1 | EENS | 6 | N-1 EENS 6 | 2641.0479 | 7012.5456
[29 empty] | N-1 | IP | 6 | N-1 IP 6 | -52.4992 | 318.4394
[29 empty] | N-1 | SAIDI | 6 | N-1 SAIDI 6 | 486.0227 | 651.6235
[29 empty] | N-1 | SAIFI | 6 | N-1 SAIFI 6 | 1.9948 | 6.5135
[29 empty] | N-1 | PFD | 6 | N-1 PFD 6 | 367.8665 | 335.777
[29 empty] | N-1 | Available Flex-1 | 6 | N-1 Available Flex-1 6 | 108576.8331 | 190663.8044
[29 empty] | N-1 | Available Flex-2-1 | 6 | N-1 Available Flex-2-1 6 | 0 | 1985141.9549
[29 empty] | N-1 | Available Flex-2-2 | 6 | N-1 Available Flex-2-2 6 | 628140.4285 | 343937.7565
[29 empty] | N-0 | EENS | 6 | N-0 EENS 6 | 10787.9436 | 10278.0469
[29 empty] | N-0 | IP | 6 | N-0 IP 6 | 903.2213 | 432.4811
[29 empty] | N-0 | SAIDI | 6 | N-0 SAIDI 6 | 610.7 | 1146.1125
[29 empty] | N-0 | SAIFI | 6 | N-0 SAIFI 6 | 10.892 | 11.6533
[29 empty] | N-0 | PFD | 6 | N-0 PFD 6 | 126.5246 | 157.8487
[29 empty] | N-1 | EENS | 7 | N-1 EENS 7 | 1889.9754 | 7763.618
[29 empty] | N-1 | IP | 7 | N-1 IP 7 | -46.1734 | 312.1137
[29 empty] | N-1 | SAIDI | 7 | N-1 SAIDI 7 | 606.4801 | 531.1662
[29 empty] | N-1 | SAIFI | 7 | N-1 SAIFI 7 | 2.1362 | 6.372
[29 empty] | N-1 | PFD | 7 | N-1 PFD 7 | 388.6179 | 315.0255
[29 empty] | N-1 | Available Flex-1 | 7 | N-1 Available Flex-1 7 | 97911.486 | 201329.1515
[29 empty] | N-1 | Available Flex-2-1 | 7 | N-1 Available Flex-2-1 7 | 1159523.3929 | 825618.562
[29 empty] | N-1 | Available Flex-2-2 | 7 | N-1 Available Flex-2-2 7 | 625479.561 | 346598.624
[29 empty] | N-0 | EENS | 7 | N-0 EENS 7 | 20662.7139 | 521.0937
[29 empty] | N-0 | IP | 7 | N-0 IP 7 | 1237.886 | 97.8164
[29 empty] | N-0 | SAIDI | 7 | N-0 SAIDI 7 | 1743.7602 | 13.0522
[29 empty] | N-0 | SAIFI | 7 | N-0 SAIFI 7 | 21.9701 | 0.57514
[29 empty] | N-0 | PFD | 7 | N-0 PFD 7 | 273.7617 | 10.6116
[29 empty] | N-1 | EENS | 8 | N-1 EENS 8 | 2643.0908 | 7010.5026
[29 empty] | N-1 | IP | 8 | N-1 IP 8 | 27.8523 | 238.0879
[29 empty] | N-1 | SAIDI | 8 | N-1 SAIDI 8 | 623.6015 | 514.0447
[29 empty] | N-1 | SAIFI | 8 | N-1 SAIFI 8 | 1.9533 | 6.555
[29 empty] | N-1 | PFD | 8 | N-1 PFD 8 | 444.5369 | 259.1066
[29 empty] | N-1 | Available Flex-1 | 8 | N-1 Available Flex-1 8 | 143555.8795 | 155684.758
[29 empty] | N-1 | Available Flex-2-1 | 8 | N-1 Available Flex-2-1 8 | 512526.5558 | 1472615.3991
[29 empty] | N-1 | Available Flex-2-2 | 8 | N-1 Available Flex-2-2 8 | 587117.8253 | 384960.3597
[29 empty] | N-0 | EENS | 8 | N-0 EENS 8 | 14173.305 | 5461.3277
[29 empty] | N-0 | IP | 8 | N-0 IP 8 | 727.3796 | 583.6308
[29 empty] | N-0 | SAIDI | 8 | N-0 SAIDI 8 | 1505.3441 | 248.9061
[29 empty] | N-0 | SAIFI | 8 | N-0 SAIFI 8 | 16.9262 | 5.4259
[29 empty] | N-0 | PFD | 8 | N-0 PFD 8 | 163.2642 | 92.3689
[29 empty] | N-1 | EENS | 9 | N-1 EENS 9 | 7597.9801 | 2055.6133
[29 empty] | N-1 | IP | 9 | N-1 IP 9 | 144.9144 | 121.0259
[29 empty] | N-1 | SAIDI | 9 | N-1 SAIDI 9 | 1059.0133 | 78.633
[29 empty] | N-1 | SAIFI | 9 | N-1 SAIFI 9 | 6.1176 | 2.3906
[29 empty] | N-1 | PFD | 9 | N-1 PFD 9 | 617.1566 | 86.4869
[29 empty] | N-1 | Available Flex-1 | 9 | N-1 Available Flex-1 9 | 252249.9385 | 46990.699
[29 empty] | N-1 | Available Flex-2-1 | 9 | N-1 Available Flex-2-1 9 | 1329505.5441 | 655636.4109
[29 empty] | N-1 | Available Flex-2-2 | 9 | N-1 Available Flex-2-2 9 | 735410.3655 | 236667.8195
[29 empty] | N-0 | EENS | 9 | N-0 EENS 9 | 20371.8447 | 811.9629
[29 empty] | N-0 | IP | 9 | N-0 IP 9 | 1184.7372 | 150.9652
[29 empty] | N-0 | SAIDI | 9 | N-0 SAIDI 9 | 1742.0508 | 14.7616
[29 empty] | N-0 | SAIFI | 9 | N-0 SAIFI 9 | 21.6476 | 0.89768
[29 empty] | N-0 | PFD | 9 | N-0 PFD 9 | 267.1157 | 17.2576
[29 empty] | N-1 | EENS | 10 | N-1 EENS 10 | 3417.8021 | 6235.7913
[29 empty] | N-1 | IP | 10 | N-1 IP 10 | -54.568 | 320.5083
[29 empty] | N-1 | SAIDI | 10 | N-1 SAIDI 10 | 635.0181 | 502.6282
[29 empty] | N-1 | SAIFI | 10 | N-1 SAIFI 10 | 2.697 | 5.8112
[29 empty] | N-1 | PFD | 10 | N-1 PFD 10 | 387.0171 | 316.6264
[29 empty] | N-1 | Available Flex-1 | 10 | N-1 Available Flex-1 10 | 112489.2183 | 186751.4191
[29 empty] | N-1 | Available Flex-2-1 | 10 | N-1 Available Flex-2-1 10 | 0 | 1985141.9549
[29 empty] | N-1 | Available Flex-2-2 | 10 | N-1 Available Flex-2-2 10 | 625479.561 | 346598.624
[29 empty] | N-0 | EENS | 10 | N-0 EENS 10 | 21183.8076 | 0
[29 empty] | N-0 | IP | 10 | N-0 IP 10 | 1335.7024 | 0
[29 empty] | N-0 | SAIDI | 10 | N-0 SAIDI 10 | 1756.8124 | 0
[29 empty] | N-0 | SAIFI | 10 | N-0 SAIFI 10 | 22.5453 | 0
[29 empty] | N-0 | PFD | 10 | N-0 PFD 10 | 284.3733 | 0
[29 empty] | N-1 | EENS | 11 | N-1 EENS 11 | 3417.8021 | 6235.7913
[29 empty] | N-1 | IP | 11 | N-1 IP 11 | -54.568 | 320.5083
[29 empty] | N-1 | SAIDI | 11 | N-1 SAIDI 11 | 635.0181 | 502.6282
[29 empty] | N-1 | SAIFI | 11 | N-1 SAIFI 11 | 2.697 | 5.8112
[29 empty] | N-1 | PFD | 11 | N-1 PFD 11 | 387.0171 | 316.6264
[29 empty] | N-1 | Available Flex-1 | 11 | N-1 Available Flex-1 11 | 112489.2183 | 186751.4191
[29 empty] | N-1 | Available Flex-2-1 | 11 | N-1 Available Flex-2-1 11 | 0 | 1985141.9549
[29 empty] | N-1 | Available Flex-2-2 | 11 | N-1 Available Flex-2-2 11 | 625479.561 | 346598.624
[29 empty] | N-0 | EENS | 11 | N-0 EENS 11 | 16790.5818 | 4393.2258
[29 empty] | N-0 | IP | 11 | N-0 IP 11 | 1114.1124 | 221.59
[29 empty] | N-0 | SAIDI | 11 | N-0 SAIDI 11 | 1469.8767 | 286.9358
[29 empty] | N-0 | SAIFI | 11 | N-0 SAIFI 11 | 18.6232 | 3.922
[29 empty] | N-0 | PFD | 11 | N-0 PFD 11 | 212.762 | 71.6113
[29 empty] | N-1 | EENS | 12 | N-1 EENS 12 | 9653.5934 | 0
[29 empty] | N-1 | IP | 12 | N-1 IP 12 | 265.9402 | 0
[29 empty] | N-1 | SAIDI | 12 | N-1 SAIDI 12 | 1137.6463 | 0
[29 empty] | N-1 | SAIFI | 12 | N-1 SAIFI 12 | 8.5082 | 0
[29 empty] | N-1 | PFD | 12 | N-1 PFD 12 | 703.6435 | 0
[29 empty] | N-1 | Available Flex-1 | 12 | N-1 Available Flex-1 12 | 133288.857 | 165951.7805
[29 empty] | N-1 | Available Flex-2-1 | 12 | N-1 Available Flex-2-1 12 | 1302863.5904 | 682278.3646
[29 empty] | N-1 | Available Flex-2-2 | 12 | N-1 Available Flex-2-2 12 | 691943.5847 | 280134.6003
[29 empty] | N-0 | EENS | 12 | N-0 EENS 12 | 21183.8076 | 0
[29 empty] | N-0 | IP | 12 | N-0 IP 12 | 1335.7024 | 0
[29 empty] | N-0 | SAIDI | 12 | N-0 SAIDI 12 | 1756.8124 | 0
[29 empty] | N-0 | SAIFI | 12 | N-0 SAIFI 12 | 22.5453 | 0
[29 empty] | N-0 | PFD | 12 | N-0 PFD 12 | 284.3733 | 0
[29 empty] | N-1 | EENS | 13 | N-1 EENS 13 | 1471.0441 | 8182.5493
[29 empty] | N-1 | IP | 13 | N-1 IP 13 | -32.719 | 298.6592
[29 empty] | N-1 | SAIDI | 13 | N-1 SAIDI 13 | 374.1303 | 763.516
[29 empty] | N-1 | SAIFI | 13 | N-1 SAIFI 13 | 0.84873 | 7.6595
[29 empty] | N-1 | PFD | 13 | N-1 PFD 13 | 364.9905 | 338.653
[29 empty] | N-1 | Available Flex-1 | 13 | N-1 Available Flex-1 13 | 98755.5743 | 200485.0632
[29 empty] | N-1 | Available Flex-2-1 | 13 | N-1 Available Flex-2-1 13 | 0 | 1985141.9549
[29 empty] | N-1 | Available Flex-2-2 | 13 | N-1 Available Flex-2-2 13 | 625479.561 | 346598.624
[29 empty] | N-0 | EENS | 13 | N-0 EENS 13 | 10376.9204 | 10278.0469
[29 empty] | N-0 | IP | 13 | N-0 IP 13 | 839.4895 | 496.2129
[29 empty] | N-0 | SAIDI | 13 | N-0 SAIDI 13 | 601.4071 | 1155.4053
[29 empty] | N-0 | SAIFI | 13 | N-0 SAIFI 13 | 10.5431 | 12.0021
[29 empty] | N-0 | PFD | 13 | N-0 PFD 13 | 121.8543 | 162.5189
Note on A61: Criteria is positive in less than 4 categories

## Incr. C-B Monetized
Incremental Cost-Benefit analysis taking into consideration applicable Monetized Benefits
# | Project | Present Value | Aggregate | [25 empty] | For Calculations only
0 | Baseline | 0 | 0 | [25 empty] | Category |  |  |  | NPV of benefits between Project and Baseline | NPV of Project Performance
13 | Valley South to Valley North | 185 | 190 | [25 empty] | N-0 | EENS | 1 | N-0 EENS 1 | 645.3857 | 0
6 | Valley South to Valley North and Distributed BESS in Valley South | 213 | 324 | [25 empty] | N-0 | Losses | 1 | N-0 Losses 1 | 5.3727 | 0
3 | Valley South to Valley North to Vista | 270 | 285 | [25 empty] | N-1 | EENS | 1 | N-1 EENS 1 | 21.431 | 0
8 | Mira Loma | 290 | 328 | [25 empty] | N-1 | Flexibility-1 | 1 | N-1 Flexibility-1 1 | 8409.9881 | 0
7 | Menifee | 315 | 358 | [25 empty] | N-1 | Flexibility-2-1 | 1 | N-1 Flexibility-2-1 1 | 425.6729 | 0
11 | Valley South to Valley North to Vista and Centralized BESS in Valley South | 400 | 951 | [25 empty] | N-1 | Flexibility-2-2 | 1 | N-1 Flexibility-2-2 1 | 330.8807 | 0
2 | SDG&E | 469 | 540 | [25 empty] | Total | Aggregate | 1 | Total Aggregate 1 | 9833.3585 | 0
1 | Alberhill System Project | 545 | 545 | [25 empty] | N-0 | EENS | 2 | N-0 EENS 2 | 607.7694 | 0
12 | SDG&E and Centralized BESS in Valley South | 701 | 1473 | [25 empty] | N-0 | Losses | 2 | N-0 Losses 2 | 3.6529 | 0
10 | Valley South to Valley North and Centralized BESS in Valley South and Valley North | 726 | 2582 | [25 empty] | N-1 | EENS | 2 | N-1 EENS 2 | 23.6272 | 0
9 | SCE Orange County | 806 | 951 | [25 empty] | N-1 | Flexibility-1 | 2 | N-1 Flexibility-1 2 | 3441.866 | 0
5 | Mira Loma and Centralized BESS in Valley South | 829 | 2156 | [25 empty] | N-1 | Flexibility-2-1 | 2 | N-1 Flexibility-2-1 2 | 295.878 | 0
4 | Centralized BESS in Valley South | 923 | 2363 | [25 empty] | N-1 | Flexibility-2-2 | 2 | N-1 Flexibility-2-2 2 | 224.0723 | 0
[29 empty] | Total | Aggregate | 2 | Total Aggregate 2 | 4593.2129 | 0
[29 empty] | N-0 | EENS | 3 | N-0 EENS 3 | 483.2223 | 0
Present Value of Monetized Benefits($) | [28 empty] | N-0 | Losses | 3 | N-0 Losses 3 | 0.34872 | 0
|  | Alberhill System Project | SDG&E | Valley South to Valley North to Vista | Centralized BESS in Valley South | Mira Loma and Centralized BESS in Valley South | Valley South to Valley North and Distributed BESS in Valley South | Menifee | Mira Loma | SCE Orange County | Valley South to Valley North and Centralized BESS in Valley South and Valley North | Valley South to Valley North to Vista and Centralized BESS in Valley South | SDG&E and Centralized BESS in Valley South | Valley South to Valley North | [14 empty] | N-1 | EENS | 3 | N-1 EENS 3 | 5.1637 | 0
Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | [14 empty] | N-1 | Flexibility-1 | 3 | N-1 Flexibility-1 3 | 2775.4693 | 0
N-0 | EENS ($M) | 645385726.1838 | 607769413.7429 | 483222347.4855 | 647092519.6355 | 647092519.6355 | 301630203.7165 | 621473538.1669 | 430214728.8342 | 609900047.0946 | 647092519.6355 | 508922896.9483 | 647092519.6355 | 288035838.7318 | [14 empty] | N-1 | Flexibility-2-1 | 3 | N-1 Flexibility-2-1 3 | 0 | 0
N-0 | Losses ($M) | 5372738.9707 | 3652887.0567 | 348715.3314 | 920382.92 | 759493.06 | 354648.5554 | 585160.8729 | 706079.488 | 3228185.9265 | 355383.2586 | 355383.2586 | 3659341.452 | 348715.3314 | [14 empty] | N-1 | Flexibility-2-2 | 3 | N-1 Flexibility-2-2 3 | 201.4215 | 0
N-1 | EENS ($M) | 21431024.9197 | 23627188.705 | 5163660.3692 | 23725380.3606 | 22111076.2101 | 9757882.5188 | 5404938.434 | 4008191.9914 | 21350864.7607 | 10291163.1025 | 10291163.1025 | 23955422.3702 | 5163660.3692 | [14 empty] | Total | Aggregate | 3 | Total Aggregate 3 | 3465.2768 | 0
N-1 | Flexibility-1 ($M) | 8409988129.8943 | 3441866030.8344 | 2775469316.1322 | 2743103432.9559 | 5956670805.6583 | 3113974750.9461 | 2751760695.3042 | 4034551236.5712 | 7089341227.1267 | 3254403300.2807 | 3254403300.2807 | 3796866784.3223 | 2775469316.1322 | [14 empty] | N-0 | EENS | 4 | N-0 EENS 4 | 647.0925 | 0
N-1 | Flexibility-2-1 ($M) | 425672858.1785 | 295878035.7356 | 0 | 0 | 116477988.2859 | 0 | 263385526.7485 | 116477988.2859 | 302036731.1437 | 0 | 0 | 295878035.7356 | 0 | [14 empty] | N-0 | Losses | 4 | N-0 Losses 4 | 0.92038 | 0
N-1 | Flexibility-2-2 ($M) | 330880723.2643 | 224072258.9458 | 201421523.7425 | 7241189.2668 | 188669783.2371 | 202521982.9576 | 201421523.7425 | 188411324.8681 | 239375699.0796 | 201421523.7425 | 201421523.7425 | 224127689.7039 | 201421523.7425 | [14 empty] | N-1 | EENS | 4 | N-1 EENS 4 | 23.7254 | 0
Total | Aggregate ($M) | 9833.3585 | 4593.2129 | 3465.2768 | 3421.1625 | 6931.0222 | 3627.8848 | 3843.4462 | 4773.6635 | 8262.0046 | 4113.2085 | 3975.0389 | 4987.9205 | 3270.0903 | [14 empty] | N-1 | Flexibility-1 | 4 | N-1 Flexibility-1 4 | 2743.1034 | 0
[29 empty] | N-1 | Flexibility-2-1 | 4 | N-1 Flexibility-2-1 4 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 4 | N-1 Flexibility-2-2 4 | 7.2412 | 0
Ranking of Projects by Cost | [28 empty] | Total | Aggregate | 4 | Total Aggregate 4 | 3421.1625 | 0
[29 empty] | N-0 | EENS | 5 | N-0 EENS 5 | 647.0925 | 0
Category |  | 0 | 13 | 6 | 3 | 8 | 7 | 11 | 2 | 1 | 12 | 10 | 9 | 5 | 4 | [13 empty] | N-0 | Losses | 5 | N-0 Losses 5 | 0.75949 | 0
[29 empty] | N-1 | EENS | 5 | N-1 EENS 5 | 22.1111 | 0
[29 empty] | N-1 | Flexibility-1 | 5 | N-1 Flexibility-1 5 | 5956.6708 | 0
Category |  | 1: Alternative selection | [13 empty] | Preferred Trend | N-1 | Flexibility-2-1 | 5 | N-1 Flexibility-2-1 5 | 116.478 | 0
|  | 1: 0 --> 13; 3: 13 --> 6; 5: 6 --> 3; 7: 6 --> 8; 9: 8 --> 7; 11: 8 --> 11; 13: 8 --> 2 |  | 8 --> 1 |  | 1 --> 12 |  | 1 --> 10 |  | 1 --> 9 |  | 1 --> 5 |  | 1 --> 4 |  |  | N-1 | Flexibility-2-2 | 5 | N-1 Flexibility-2-2 5 | 188.6698 | 0
|  | 0 | 13 | 13 | 6 | 6 | 3 | 6 | 8 | 8 | 7 | 8 | 11 | 8 | 2 | 8 | 1 | 1 | 12 | 1 | 10 | 1 | 9 | 1 | 5 | 1 | 4 |  | Total | Aggregate | 5 | Total Aggregate 5 | 6931.0222 | 0
N-0 | EENS | 1: 1.557; 3: 0.48551; 5: 3.1858; 7: 1.6699; 9: 7.6504; 11: 0.71553; 13: 0.99193 |  | 0.84381 |  | 0.010941 |  | 0.0094298 |  | -0.13596 |  | 0.0060098 |  | 0.0045153 |  | ↑ | N-0 | EENS | 0 | N-0 EENS 0 | 0 | 0
N-0 | Losses | 1: 0.0018849; 3: 0.0002119; 5: -0.00010409; 7: 0.004564; 9: -0.0048367; 11: -0.0031881; 13: 0.016463 |  | 0.018301 |  | -0.010983 |  | -0.02772 |  | -0.0082167 |  | -0.016244 |  | -0.011779 |  | ↑ | N-0 | Losses | 0 | N-0 Losses 0 | 0 | 0
N-1 | EENS | 1: 0.027912; 3: 0.16408; 5: -0.0806; 7: -0.074671; 9: 0.05587; 11: 0.057118; 13: 0.1096 |  | 0.068325 |  | 0.016182 |  | -0.061546 |  | -0.00030713 |  | 0.0023945 |  | 0.0060697 |  | ↑ | N-1 | EENS | 0 | N-1 EENS 0 | 0 | 0
N-1 | Flexibility-1 | 1: 15.0025; 3: 12.0895; 5: -5.9387; 7: 11.9555; 9: -51.3116; 11: -7.0923; 13: -3.3111 |  | 17.1586 |  | -29.5713 |  | -28.4839 |  | -5.0599 |  | -8.6384 |  | -14.9918 |  | ↑ | N-1 | Flexibility-1 | 0 | N-1 Flexibility-1 0 | 0 | 0
N-1 | Flexibility-2-1 | 1: 0; 3: 0; 5: 0; 7: 1.5127; 9: 5.8763; 11: -1.0589; 13: 1.0022 |  | 1.2125 |  | -0.83202 |  | -2.3518 |  | -0.4737 |  | -1.0887 |  | -1.1261 |  | ↑ | N-1 | Flexibility-2-1 | 0 | N-1 Flexibility-2-1 0 | 0 | 0
N-1 | Flexibility-2-2 | 1: 1.0888; 3: 0.039302; 5: -0.019306; 7: -0.18326; 9: 0.52041; 11: 0.11827; 13: 0.19922 |  | 0.5587 |  | -0.68431 |  | -0.71524 |  | -0.35059 |  | -0.50074 |  | -0.85619 |  | ↑ | N-1 | Flexibility-2-2 | 0 | N-1 Flexibility-2-2 0 | 0 | 0
Total | Aggregate | 1: 17.6762; 3: 12.7784; 5: -2.8528; 7: 14.8802; 9: -37.2087; 11: -7.2602; 13: -1.0081 |  | 19.8419 |  | -31.0605 |  | -31.603 |  | -6.0205 |  | -10.2195 |  | -16.9635 |  | ↑ | Total | Aggregate | 0 | Total Aggregate 0 | 0 | 0
Decision to move forward (Y/N) | [15 empty] | Y |  | N |  | N |  | N |  | N |  | N |  |  | N-0 | EENS | 6 | N-0 EENS 6 | 301.6302 | 0 | bar: 1; 3; 5; 7; 9; 11; 13
[29 empty] | N-0 | Losses | 6 | N-0 Losses 6 | 0.35465 | 0
[29 empty] | N-1 | EENS | 6 | N-1 EENS 6 | 9.7579 | 0
[29 empty] | N-1 | Flexibility-1 | 6 | N-1 Flexibility-1 6 | 3113.9748 | 0
[29 empty] | N-1 | Flexibility-2-1 | 6 | N-1 Flexibility-2-1 6 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 6 | N-1 Flexibility-2-2 6 | 202.522 | 0
[29 empty] | Total | Aggregate | 6 | Total Aggregate 6 | 3627.8848 | 0
[29 empty] | N-0 | EENS | 7 | N-0 EENS 7 | 621.4735 | 0
[29 empty] | N-0 | Losses | 7 | N-0 Losses 7 | 0.58516 | 0
[29 empty] | N-1 | EENS | 7 | N-1 EENS 7 | 5.4049 | 0
[29 empty] | N-1 | Flexibility-1 | 7 | N-1 Flexibility-1 7 | 2751.7607 | 0
[29 empty] | N-1 | Flexibility-2-1 | 7 | N-1 Flexibility-2-1 7 | 263.3855 | 0
[29 empty] | N-1 | Flexibility-2-2 | 7 | N-1 Flexibility-2-2 7 | 201.4215 | 0
[29 empty] | Total | Aggregate | 7 | Total Aggregate 7 | 3843.4462 | 0
[29 empty] | N-0 | EENS | 8 | N-0 EENS 8 | 430.2147 | 0
[29 empty] | N-0 | Losses | 8 | N-0 Losses 8 | 0.70608 | 0
[29 empty] | N-1 | EENS | 8 | N-1 EENS 8 | 4.0082 | 0
[29 empty] | N-1 | Flexibility-1 | 8 | N-1 Flexibility-1 8 | 4034.5512 | 0
[29 empty] | N-1 | Flexibility-2-1 | 8 | N-1 Flexibility-2-1 8 | 116.478 | 0
[29 empty] | N-1 | Flexibility-2-2 | 8 | N-1 Flexibility-2-2 8 | 188.4113 | 0
[29 empty] | Total | Aggregate | 8 | Total Aggregate 8 | 4773.6635 | 0
[29 empty] | N-0 | EENS | 9 | N-0 EENS 9 | 609.9 | 0
[29 empty] | N-0 | Losses | 9 | N-0 Losses 9 | 3.2282 | 0
[29 empty] | N-1 | EENS | 9 | N-1 EENS 9 | 21.3509 | 0
[29 empty] | N-1 | Flexibility-1 | 9 | N-1 Flexibility-1 9 | 7089.3412 | 0
[29 empty] | N-1 | Flexibility-2-1 | 9 | N-1 Flexibility-2-1 9 | 302.0367 | 0
[29 empty] | N-1 | Flexibility-2-2 | 9 | N-1 Flexibility-2-2 9 | 239.3757 | 0
[29 empty] | Total | Aggregate | 9 | Total Aggregate 9 | 8262.0046 | 0
[29 empty] | N-0 | EENS | 10 | N-0 EENS 10 | 647.0925 | 0
[29 empty] | N-0 | Losses | 10 | N-0 Losses 10 | 0.35538 | 0
[29 empty] | N-1 | EENS | 10 | N-1 EENS 10 | 10.2912 | 0
[29 empty] | N-1 | Flexibility-1 | 10 | N-1 Flexibility-1 10 | 3254.4033 | 0
[29 empty] | N-1 | Flexibility-2-1 | 10 | N-1 Flexibility-2-1 10 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 10 | N-1 Flexibility-2-2 10 | 201.4215 | 0
[29 empty] | Total | Aggregate | 10 | Total Aggregate 10 | 4113.2085 | 0
[29 empty] | N-0 | EENS | 11 | N-0 EENS 11 | 508.9229 | 0
[29 empty] | N-0 | Losses | 11 | N-0 Losses 11 | 0.35538 | 0
[29 empty] | N-1 | EENS | 11 | N-1 EENS 11 | 10.2912 | 0
[29 empty] | N-1 | Flexibility-1 | 11 | N-1 Flexibility-1 11 | 3254.4033 | 0
[29 empty] | N-1 | Flexibility-2-1 | 11 | N-1 Flexibility-2-1 11 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 11 | N-1 Flexibility-2-2 11 | 201.4215 | 0
[29 empty] | Total | Aggregate | 11 | Total Aggregate 11 | 3975.0389 | 0
[29 empty] | N-0 | EENS | 12 | N-0 EENS 12 | 647.0925 | 0
[29 empty] | N-0 | Losses | 12 | N-0 Losses 12 | 3.6593 | 0
[29 empty] | N-1 | EENS | 12 | N-1 EENS 12 | 23.9554 | 0
[29 empty] | N-1 | Flexibility-1 | 12 | N-1 Flexibility-1 12 | 3796.8668 | 0
[29 empty] | N-1 | Flexibility-2-1 | 12 | N-1 Flexibility-2-1 12 | 295.878 | 0
[29 empty] | N-1 | Flexibility-2-2 | 12 | N-1 Flexibility-2-2 12 | 224.1277 | 0
[29 empty] | Total | Aggregate | 12 | Total Aggregate 12 | 4987.9205 | 0
[29 empty] | N-0 | EENS | 13 | N-0 EENS 13 | 288.0358 | 0
[29 empty] | N-0 | Losses | 13 | N-0 Losses 13 | 0.34872 | 0
[29 empty] | N-1 | EENS | 13 | N-1 EENS 13 | 5.1637 | 0
[29 empty] | N-1 | Flexibility-1 | 13 | N-1 Flexibility-1 13 | 2775.4693 | 0
[29 empty] | N-1 | Flexibility-2-1 | 13 | N-1 Flexibility-2-1 13 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 13 | N-1 Flexibility-2-2 13 | 201.4215 | 0
[29 empty] | Total | Aggregate | 13 | Total Aggregate 13 | 3270.0903 | 0
Note on A48: Criteria is negative value in less than 2 categories

## Levelized Cost Analysis
Evaluation of Present Value of Cost $/ Present Value of Benefit
|  | Levelized cost analysis ( Present Value of Cost $/Present Value of Benefit) for each Alternative | [12 empty] | Alternative Ranking
|  | Alberhill System Project | SDG&E | Valley South to Valley North to Vista | Centralized BESS in Valley South | Mira Loma and Centralized BESS in Valley South | Valley South to Valley North and Distributed BESS in Valley South | Menifee | Mira Loma | SCE Orange County | Valley South to Valley North and Centralized BESS in Valley South and Valley North | Valley South to Valley North to Vista and Centralized BESS in Valley South | SDG&E and Centralized BESS in Valley South | Valley South to Valley North
Reliability Metrics |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | Rank #1 | Rank #2 | Rank #3
N-1 | EENS ↓ | 0.060994 | 0.048865 | 0.18354 | 0.095685 | 0.097848 | 0.08065 | 0.16667 | 0.10972 | 0.10608 | 0.21242 | 0.11703 | 0.072615 | 0.12576 | 2 | 1 | 12
N-1 | IP ↓ | 2.6217 | 1.8075 | 8.2521 | 3.4935 | 6.2006 | 4.0572 | 6.8221 | 10.412 | 5.5619 | 13.3045 | 7.3303 | 2.6359 | 5.6542 | 2 | 1 | 12
N-1 | SAIDI ↓ | 0.50681 | 0.41269 | 0.72167 | 0.81145 | 0.76613 | 0.43825 | 0.51939 | 0.46504 | 0.76109 | 1.1433 | 0.6299 | 0.61618 | 0.49448 | 2 | 6 | 8
N-1 | SAIFI ↓ | 81.4328 | 55.498 | 318.1211 | 108.7091 | 113.7849 | 106.7797 | 147.4586 | 148.4704 | 131.7513 | 269.1832 | 148.3103 | 82.3909 | 217.9718 | 2 | 1 | 12
N-1 | PFD ↓ | 0.80291 | 0.66947 | 0.73975 | 1.3135 | 1.6748 | 0.57901 | 0.81056 | 0.65236 | 1.306 | 1.8759 | 1.0335 | 0.99624 | 0.50686 | 13 | 6 | 8
N-1 | Flex-1↓ | 0.0018213 | 0.003835 | 0.002734 | 0.0094566 | 0.0038811 | 0.0019617 | 0.0032172 | 0.0020201 | 0.0031952 | 0.006454 | 0.0035559 | 0.0052593 | 0.0018733 | 1 | 13 | 6
N-1 | Flex-2-1↓ | 0.00029256 | 0.00035998 |  |  | 0.0016175 |  | 0.00027166 | 0.00056582 | 0.00060624 |  |  | 0.00053805 |  | 7 | 1 | 2
N-1 | Flex-2-2↓ | 0.00056092 | 0.00067792 | 0.00043167 | 0.045779 | 0.0014105 | 0.0003391 | 0.00050361 | 0.00049394 | 0.001096 | 0.0011607 | 0.00063951 | 0.0010131 | 0.00029577 | 13 | 6 | 3
N-0 | EENS ↓ | 0.025769 | 0.02312 | 0.016603 | 0.043571 | 0.039134 | 0.019744 | 0.015245 | 0.020461 | 0.039564 | 0.034271 | 0.023823 | 0.033091 | 0.017828 | 7 | 3 | 13
N-0 | IP ↓ | 0.4104 | 0.39723 | 0.26728 | 0.69102 | 0.62065 | 0.23582 | 0.25447 | 0.39869 | 0.68032 | 0.54353 | 0.35903 | 0.52482 | 0.22037 | 13 | 6 | 7
N-0 | SAIDI ↓ | 0.31046 | 0.26901 | 0.18504 | 0.52538 | 0.47188 | 0.34878 | 0.18064 | 0.19265 | 0.46267 | 0.41325 | 0.27213 | 0.39902 | 0.30761 | 7 | 3 | 8
N-0 | SAIFI ↓ | 24.302 | 21.5487 | 14.8762 | 40.9399 | 36.7705 | 19.5556 | 14.3377 | 17.1332 | 37.2328 | 32.2019 | 21.4786 | 31.093 | 17.547 | 7 | 3 | 8
N-0 | PFD ↓ | 1.9566 | 1.7664 | 1.3525 | 3.2457 | 2.9152 | 1.6835 | 1.1506 | 1.7763 | 3.0174 | 2.553 | 1.88 | 2.4651 | 1.5182 | 7 | 3 | 13
Count of Rank #1 |  | 1 | 4 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3

## Cost Assumptions
Financial and Study Parameters | Value | Unit | Source
Discount Rate (Weighted Aggregate Cost of Capital) | 10% |  | CPUC
Customer price (Average Locational Marginal Price in Valley South - 2022) | 40 | $/MWh | CAISO
Inflation Rate | 1.025 |  | Quanta
Load distribution : Residential | 90% |  | SCE
Load distribution : Commercial | 10% |  | SCE
Customer Interruption cost for Flex-1 events (6hours) : N-1 : Residential | 4.1725 | $/kWh | LBNL
Customer Interruption cost (Average cost over 24 hr duration) : N-0 : Residential (Flex-2 Component 1) | 3.5212 | $/kWh | LBNL
Customer Interruption cost for Flex-1 events (6hours) : N-1 : Commercial | 154.7025 | $/kWh | LBNL
Customer Interruption cost (Average cost over 24 hr duration) : N-0 : Residential (Flex-2 Component 1) | 142.8531 | $/kWh | LBNL
Annual Outage rate for Transformer N-2 Outage events | 0.0169 |  | NERC
Annual Outage rate for High Impact Low Probability(HILP) Events | 0.01 |  | NERC
Flex-1 Duration of evaluation | 1 | hour | Quanta
Normalization Factor for Cost Benefit | 1 |  | Quanta

## Baseline System Analysis
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
Valley South (alone) | Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential | Cost of Reliability (N-2) | $/kwh |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical | Cost of Reliability (N-2) | $/kwh |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Monetized EENS | 4652002.7758 | 2664.1723 | 6696.6565 | 15296.142 | 23895.6274 | 32495.1129 | 41094.5983 | 49694.0838 | 58293.5692 | 105854.9234 | 153416.2776 | 200977.6318 | 248538.986 | 392537.6555 | 536536.325 | 680534.9945 | 824533.664 | 968532.3336 | 1112531.0031 | 1456952.4967 | 1801373.9903 | 2145795.484 | 2490216.9776 | 2834638.4712 | 3388540.27 | 3942442.0689 | 4496343.8677 | 5050245.6665 | 5604147.4653
Commerical(N-1) | Monetized EENS | 19303419.5944 | 11054.9454 | 27787.6812 | 63471.1243 | 99154.5673 | 134838.0103 | 170521.4534 | 206204.8964 | 241888.3395 | 439243.5047 | 636598.6698 | 833953.835 | 1031309.0002 | 1628829.4388 | 2226349.8773 | 2823870.3159 | 3421390.7544 | 4018911.193 | 4616431.6315 | 6045603.7385 | 7474775.8455 | 8903947.9525 | 10333120.0595 | 11762292.1666 | 14060699.8314 | 16359107.4962 | 18657515.161 | 20955922.8258 | 23254330.4906
Aggregate | Monetized EENS | 23955422.3702 | 13719.1178 | 34484.3377 | 78767.2662 | 123050.1947 | 167333.1232 | 211616.0517 | 255898.9802 | 300181.9087 | 545098.4281 | 790014.9475 | 1034931.4668 | 1279847.9862 | 2021367.0943 | 2762886.2023 | 3504405.3104 | 4245924.4184 | 4987443.5265 | 5728962.6346 | 7502556.2352 | 9276149.8359 | 11049743.4365 | 12823337.0371 | 14596930.6378 | 17449240.1014 | 20301549.565 | 23153859.0286 | 26006168.4922 | 28858477.9559
Residential (N-0) | Monetized EENS | 122402385.4505 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17866466.9567 | 20996797.7861 | 24698098.9882 | 28840317.3417 | 33541217.3533 | 38471074.1279 | 44538095.4972 | 50065147.4545 | 56027611.2185 | 61953016.927 | 68192076.4928 | 75753576.0548 | 84072896.7752 | 90296154.7352 | 99941321.9255
Commerical(N-0) | Monetized EENS | 524690134.185 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 77675195.1106 | 90392543.5661 | 106694968.7558 | 124345366.1109 | 143712431.512 | 164558346.4294 | 190732503.3698 | 211736495.7562 | 237640870.2909 | 261024283.4324 | 285410828.6852 | 316389312.3519 | 351526819.4674 | 372036180.3666 | 405152985.562
Aggregate | Monetized EENS | 647092519.6355 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 95541662.0673 | 111389341.3522 | 131393067.744 | 153185683.4525 | 177253648.8653 | 203029420.5574 | 235270598.867 | 261801643.2106 | 293668481.5094 | 322977300.3594 | 353602905.1779 | 392142888.4066 | 435599716.2426 | 462332335.1019 | 505094307.4875
Residential (N-1) | Monetized Value for Flex-1 | 1642693710.1654 | 24962423.7752 | 38784191.367 | 53281445.8236 | 68479322.8835 | 84403792.8927 | 101081686.8255 | 118540723.0844 | 136809535.102 | 155917699.7686 | 175895766.709 | 196775288.4342 | 218588851.3913 | 241370107.9411 | 265153809.2862 | 289975839.3812 | 315873249.8501 | 342884295.9428 | 371048473.5589 | 400406557.371 | 431000640.0776 | 462874172.8212 | 496072006.802 | 530640436.1238 | 566627241.9074 | 604081737.7076 | 643054816.2717 | 683598997.6779 | 725768478.8942
Commerical(N-1) | Monetized Value for Flex-1 | 6767294419.7288 | 102836012.6244 | 159776615.8034 | 219499976.6336 | 282109645.1203 | 347712609.546 | 416419403.6648 | 488344217.1086 | 563605009.0972 | 642323625.5496 | 724625919.6939 | 810641876.2795 | 900505739.4946 | 994356144.6977 | 1092336254.0738 | 1194593896.3283 | 1301281710.5366 | 1412557294.2703 | 1528583356.1215 | 1649527872.7563 | 1775564250.6253 | 1906871492.4673 | 2043634368.7447 | 2186043594.1533 | 2334296009.3518 | 2488594768.0638 | 2649149529.7057 | 2816176657.6995 | 2989899423.637
Aggregate | Monetized Value for Flex-1 | 8409988129.8943 | 127798436.3995 | 198560807.1705 | 272781422.4572 | 350588968.0038 | 432116402.4387 | 517501090.4903 | 606884940.193 | 700414544.1993 | 798241325.3182 | 900521686.403 | 1007417164.7137 | 1119094590.8859 | 1235726252.6388 | 1357490063.36 | 1484569735.7094 | 1617154960.3867 | 1755441590.213 | 1899631829.6804 | 2049934430.1273 | 2206564890.7029 | 2369745665.2885 | 2539706375.5468 | 2716684030.2771 | 2900923251.2592 | 3092676505.7715 | 3292204345.9773 | 3499775655.3774 | 3715667902.5312
Residential | Monetized Value for Flex-2_1 | 82608829.8082 | 6479744.9494 | 6756311.4714 | 7042656.479 | 7290213.5443 | 7546373.1095 | 7810142.3049 | 8088963.6148 | 8376170.1872 | 8672681.4859 | 8978783.2432 | 9296948.6347 | 9625410.5563 | 9965248.0753 | 10315279.4171 | 10673377.1422 | 11042932.704 | 11425137.4964 | 11818687.3244 | 12216809.3342 | 12627450.765 | 13050988.7614 | 13486858.5007 | 13924642.9569 | 14374886.1035 | 14838938.5056 | 15318261.1579 | 15795023.8906 | 16286050.8467
Commerical | Monetized Value for Flex-2_1 | 372371853.136 | 29208434.985 | 30455100.6087 | 31745844.2417 | 32861745.3309 | 34016423.4959 | 35205403.2249 | 36462232.6476 | 37756859.9147 | 39093429.6498 | 40473229.8342 | 41907408.6831 | 43388000.7059 | 44919869.9628 | 46497689.4246 | 48111869.3352 | 49777697.1855 | 51500543.365 | 53274529.0163 | 55069124.472 | 56920153.1198 | 58829314.9972 | 60794064.0797 | 62767444.0391 | 64796983.4389 | 66888770.1561 | 69049389.8464 | 71198470.3102 | 73411848.9284
Aggregate | Monetized Value for Flex-2_1 | 454980682.9442 | 35688179.9344 | 37211412.0801 | 38788500.7207 | 40151958.8752 | 41562796.6054 | 43015545.5298 | 44551196.2624 | 46133030.1019 | 47766111.1357 | 49452013.0773 | 51204357.3178 | 53013411.2622 | 54885118.0381 | 56812968.8417 | 58785246.4775 | 60820629.8894 | 62925680.8614 | 65093216.3407 | 67285933.8062 | 69547603.8847 | 71880303.7586 | 74280922.5804 | 76692086.9961 | 79171869.5424 | 81727708.6618 | 84367651.0043 | 86993494.2007 | 89697899.7751
Residential | Monetized Value for Flex-2_2 | 65672043.6869 | 3271758.2464 | 3697126.04 | 4150284.9952 | 4480466.6399 | 4848183.0224 | 5212148.5122 | 5591774.3794 | 6026004.1139 | 6474039.4578 | 6947092.5377 | 7498461.4567 | 8019269.634 | 8591538.4551 | 9203213.0631 | 9813368.5566 | 10485782.903 | 11174577.2641 | 11910323.5035 | 12634903.5269 | 13400277.0927 | 14178134.0321 | 14970826.2766 | 15823161.9795 | 16694064.3114 | 17554796.6395 | 18491180.8937 | 19332692.6667 | 20272966.9801
Commerical | Monetized Value for Flex-2_2 | 265545644.464 | 13254020.7015 | 14995227.6273 | 16823153.9319 | 18163165.3525 | 19644257.8424 | 21100440.8917 | 22606458.2587 | 24363930.483 | 26194836.9795 | 28083995.024 | 30330957.7805 | 32441113.6659 | 34736744.709 | 37191747.847 | 39634988.6357 | 42351331.3574 | 45147781.5756 | 48091952.1066 | 51016691.4173 | 54128286.5056 | 57217414.167 | 60410587.8363 | 63844128.1149 | 67338713.3142 | 70844441.4974 | 74614729.6844 | 78045173.3267 | 81869455.3917
Aggregate | Monetized Value for Flex-2_2 | 331217688.1509 | 16525778.9479 | 18692353.6673 | 20973438.9271 | 22643631.9924 | 24492440.8648 | 26312589.4039 | 28198232.638 | 30389934.5969 | 32668876.4373 | 35031087.5617 | 37829419.2372 | 40460383.2999 | 43328283.1641 | 46394960.9101 | 49448357.1923 | 52837114.2603 | 56322358.8397 | 60002275.6102 | 63651594.9443 | 67528563.5984 | 71395548.199 | 75381414.1129 | 79667290.0944 | 84032777.6256 | 88399238.1369 | 93105910.5781 | 97377865.9934 | 102142422.3718
Aggregate Monetized Costs ($) |  | 9867234442.9951 | 181964654.442 | 259592903.1004 | 340363271.904 | 424309370.7925 | 511321233.0209 | 601672552.6241 | 699418959.0963 | 801385395.1878 | 909576464.7229 | 1026140174.7878 | 1150432475.8062 | 1282189056.5488 | 1419945428.9626 | 1559002541.3815 | 1707697086.0417 | 1866451696.6989 | 2032862756.8932 | 2207709933.1311 | 2391403935.6703 | 2588187806.8889 | 2785872903.8933 | 2995860530.7866 | 3210617638.3647 | 3435180043.7065 | 3675247890.5418 | 3928431482.831 | 4172485519.1657 | 4441461010.1215
Residential (N-1) | Monetized EENS | 4652002.7758
Commerical(N-1) | Monetized EENS | 19303419.5944
Aggregate | Monetized EENS | 23955422.3702
Residential (N-0) | Monetized EENS | 122402385.4505
Commerical(N-0) | Monetized EENS | 524690134.185
Aggregate | Monetized EENS | 647092519.6355
Residential (N-0) | Monetized Value for Flex-1 | 1642693710.1654
Commerical(N-0) | Monetized Value for Flex-1 | 6767294419.7288
Aggregate | Monetized Value for Flex-1 | 8409988129.8943
Residential | Monetized Value for Flex-2 | 148280873.4952
Commerical | Monetized Value for Flex-3 | 637917497.6
Aggregate | Monetized Value for Flex-4 | 786198371.0951
Aggregate ($M) |  | 9867.2344
Note on C3: Sum of the EENS accumulated under N-1 condition, considering all outages in the system
Note on C4: Representative of the peak MW load drop required while considering all outages
Note on C5: Sum of total customers interrupted for all outages x number of outage hours/ total number of customers served.
Note on C6: Sum of total hours customers were without power due to all outages/ total number of customers served.
Note on C7: Periods with flexibility shortages in the system
Note on C8: Sum of EENS accumulated due to N-0 overloads in the system (transformer and lines)
Note on C13: Sum of EENS accumulated under N-2 events in the systems (emergency, planned or unplanned maintainence events)
Note on C14: Sum of EENS accumulated under entire Valley substation outage (considered over 2 week period)
Note on C15: Sum of EENS accumulated considering N-2 transformer outage event at Valley South (Loss of Valley Transformer and unavailable spare)

## Sheet2 (hidden)
Equipment Categories
All costs are $x1,000
New Substation Equipment
500kV |  |  |  |  | 36194.3937
115kV |  |  |  |  | 4403.9172
230kV |  |  |  |  | 17710.3457
Transformer Banks
500/115 kV |  |  |  |  | 24748.4568
230/115 kV |  |  |  |  | 8756.8817
kV
Line Positions to terminate ties and Transformer Bank positions |  |  | 230 | 500 | 115
Single Breaker (add third breaker to breaker and a half) |  |  | 2145.4637 | 5398.3718 | 1437.1815
Breaker and a half (2CB) |  |  | 3607.9737 | 8587.7771 | 2149.8636
Breaker and a half (3CB) |  |  | 5291.2883 | 12131.4222 | 3436.5983
Breaker and a half (3CB) |  |  | 5291.2883 | 12131.4222 | 3436.5983
Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | Used in substation expansion | 540.3386 |  | 252.4804
Shunt Capacitors |  |  |  |  | 2006.8433
Fiber optic cable on existing poles | /mile |  |  | 99 | 99
Fiber optic cable on new poles | /mile |  |  | 134 | 134
Single Circuit, Lattice Tower | /mile |  | 2897.3658 | 4578.5833 | 1815.3927
|  |  | 2897.3658 | 4578.5833 | 1815.3927
Double Circuit, Strung on both sides, Lattice Tower | /mile |  | 4494.8333 | 9381.7495 | 2174.744
Rebuild/reconductor existing single circuit line section - Metropolitan | /mile |  |  |  | 1381.7727
Rebuild/reconductor existing double circuit line section - Metropolitan | /mile |  |  |  | 1454.8259
Disconnect switches (incl. steel structures and foundations) |  |  | 3326.9104 | 19935.5969 | 105.461

## Alberhill System Project
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Alberhill System Project | Losses (MWh) | 40954 | 41590.2941 | 41894.7511 | 42199.2081 | 42503.6652 | 42808.1222 | 43112.5792 | 43417.0362 | 43721.4932 | 44025.9502 | 44330.4072 | 44634.8643 | 44939.3213 | 45243.7783 | 45548.2353 | 45852.6923 | 46157.1493 | 46461.6063 | 46766.0633 | 47070.5204 | 47374.9774 | 47679.4344 | 47983.8914 | 48288.3484 | 48592.8054 | 48897.2624 | 49201.7195 | 49506.1765
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4 | 59.38 | 85.36 | 111.34 | 137.32 | 163.3 | 236.68 | 310.06 | 383.44 | 456.82 | 530.2 | 621.9 | 713.6 | 805.3 | 897 | 1080.3
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 12.86 | 15.12 | 17.38 | 19.64 | 21.9 | 24.34 | 26.78 | 29.22 | 31.66 | 34.1 | 36.17 | 38.24 | 40.31 | 42.38 | 42.6
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42242 | 1.5986 | 2.7748 | 3.9511 | 5.1273 | 6.3035 | 14.0977 | 21.892 | 29.6863 | 37.4805 | 45.2748 | 59.8447 | 74.4147 | 88.9846 | 103.5546 | 152.003
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.084484 | 0.15044 | 0.2164 | 0.28236 | 0.34831 | 0.41427 | 0.60056 | 0.78685 | 0.97313 | 1.1594 | 1.3457 | 1.5737 | 1.8018 | 2.0298 | 2.2578 | 2.6945
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.4 | 7.8 | 9.2 | 10.6 | 12 | 10.8 | 9.6 | 8.4 | 7.2 | 6 | 9.1 | 12.2 | 15.3 | 18.4 | 43
N-1 |  | Deficit Flex-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | Deficit Flex-2-1 | 8194.6224 | 8960.1834 | 9762.6955 | 10249.6993 | 10764.6214 | 11282.1805 | 11851.9808 | 12431.3027 | 13021.5834 | 13618.5277 | 14237.7602 | 14874.1861 | 15530.1807 | 16188.0292 | 16831.3277 | 17485.1753 | 18156.2953 | 18825.5516 | 19458.9604 | 20105.4631 | 20761.5449 | 21416.2755 | 22008.5972 | 22600.5399 | 23199.6596 | 23811.7421 | 24331.0938 | 24853.1363
N-1 |  | Deficit Flex-2-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0455 | 24.0279 | 49.492 | 75.8304 | 108.7819 | 147.9019 | 192.4084 | 241.2482 | 294.3613 | 352.5808 | 419.4738 | 496.0053 | 592.683 | 691.2159 | 803.1482
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 6.08 | 11.56 | 17.04 | 22.52 | 28 | 38.6067 | 44.0867 | 49.5667 | 62.5067 | 92.7
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 2.16 | 3.72 | 5.28 | 6.84 | 8.4 | 7.1133 | 8.6733 | 10.2333 | 11.3333 | 13.9
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041595 | 0.11979 | 0.23543 | 0.35106 | 0.46669 | 0.58233 | 1.8707 | 1.9863 | 2.1019 | 3.0137 | 5.1411
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020797 | 0.021075 | 0.04007 | 0.059065 | 0.078059 | 0.097054 | 0.13382 | 0.15281 | 0.17181 | 0.21666 | 0.32132
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 5.3333 | 6.3333 | 7.3333 | 8.1333 | 10
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9426.6841 | 43278.7043 | 82077.916 | 146649.3115 | 207427.5708 | 230139.3014 | 315962.1837 | 404739.1901 | 516562.4118 | 576781.3107 | 624802.7469
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53118.9371 | 243873.5334 | 431406.6128 | 779587.1762 | 1085338.8387 | 1082489.2453 | 1508481.3469 | 1961497.9404 | 2520388.535 | 2692935.1382 | 2747620.8669
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34018.1885 | 48617.1487 | 63216.1089 | 77815.0691 | 92414.0293 | 107012.9895 | 135849.3815 | 164685.7736 | 193522.1657 | 222358.5578 | 251194.9499 | 382199.8343 | 513204.7187 | 644209.6032 | 775214.4876 | 906219.372
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191690.9475 | 242162.5347 | 292634.1218 | 343105.709 | 393577.2961 | 444048.8833 | 563705.0836 | 683361.2839 | 803017.4842 | 922673.6845 | 1042329.8848 | 1585932.7963 | 2129535.7077 | 2673138.6192 | 3216741.5307 | 3760344.4422
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10299.0448 | 21471.1353 | 48188.8438 | 72251.305 | 79886.0511 | 116842.4931 | 155683.7717 | 180090.391 | 197289.6198 | 244281.8735 | 297257.3707 | 339450.3042 | 414718.9341 | 470485.5848 | 572079.5819
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 105432.2877 | Losses (MWh) | 9127.75 | 9297.7559 | 9589.8027 | 9881.8495 | 10173.8964 | 10465.9432 | 10757.99 | 11050.0369 | 11342.0837 | 11634.1305 | 11926.1774 | 12218.2242 | 12510.271 | 12802.3179 | 13094.3647 | 13386.4115 | 13678.4584 | 13970.5052 | 14262.552 | 14554.5989 | 14846.6457 | 15138.6925 | 15430.7394 | 15722.7862 | 16014.833 | 16306.8799 | 16598.9267 | 16890.9735
| 5372738.9707 | Losses ($) | 365110 | 381207.9912 | 403011.4591 | 425666.8454 | 449203.1189 | 473650.1643 | 499038.8099 | 525400.8566 | 552769.1063 | 581177.3929 | 610660.6132 | 641254.7586 | 672996.9484 | 705925.4635 | 740079.7813 | 775500.6115 | 812229.9334 | 850311.0334 | 889788.5448 | 930708.4873 | 973118.3092 | 1017066.9293 | 1062604.7815 | 1109783.8594 | 1158657.7633 | 1209281.7475 | 1261712.7697 | 1316009.542
N-1 | 8935.2425 | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 955.25 | 1218.52 | 1481.79 | 1745.06 | 2008.33 | 2271.6 | 2878.29 | 3484.98 | 4091.67 | 4698.36 | 4732.5 | 5435.38 | 6138.26 | 6841.14 | 7544.02 | 8155.3
N-1 | 207.8798 | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 28.9 | 31.04 | 33.18 | 35.32 | 37.46 | 39.6 | 39.14 | 38.68 | 38.22 | 37.76 | 37.3 | 46.63 | 55.96 | 65.29 | 74.62 | 85.8
N-1 | 1075.3499 | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 53.7144 | 81.2036 | 108.6928 | 136.1821 | 163.6713 | 191.1605 | 291.5014 | 391.8422 | 492.1831 | 592.5239 | 692.8648 | 917.5121 | 1142.1595 | 1366.8069 | 1591.4542 | 1782.2231
N-1 | 6.6926 | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.78791 | 0.98364 | 1.1794 | 1.3751 | 1.5708 | 1.7666 | 2.1001 | 2.4336 | 2.7672 | 3.1007 | 3.4343 | 3.9398 | 4.4454 | 4.951 | 5.4566 | 5.7534
N-1 | 678.7835 | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 92.8333 | 101.2667 | 109.7 | 118.1333 | 126.5667 | 135 | 147.6 | 160.2 | 172.8 | 185.4 | 198 | 206.3 | 214.6 | 222.9 | 231.2 | 218
N-1 | 299240.6375 | Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 | 1862863.7959 | Flex-2-1 | 186417.9134 | 189009.5039 | 191564.1433 | 193070.9807 | 194566.9412 | 196043.2233 | 197637.6779 | 199205.5697 | 200762.5026 | 202312.772 | 203891.8772 | 205453.789 | 207013.1735 | 208553.6628 | 210040.5365 | 211516.8612 | 212992.9548 | 214453.8708 | 215797.2618 | 217127.5589 | 218448.277 | 219753.3048 | 220916.2451 | 222062.5229 | 223201.6238 | 224344.8032 | 225308.0513 | 226268.6087
N-1 | 971617.2786 | Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131052.6077 | 136903.3502 | 142878.9772 | 149020.3994 | 155247.1016 | 161139.8187 | 167138.143 | 173244.1833 | 179443.2041 | 185045.3509 | 190641.4157 | 196309.2298 | 202093.9479 | 207035.6231 | 212019.5801
N-0 | 21149.4476 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740 | 6563.92 | 7387.84 | 8211.76 | 9035.68 | 9859.6 | 10775.9533 | 11697.4333 | 12618.9133 | 13532.9333 | 14429.7
N-0 | 1327.9868 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 279.4 | 291.52 | 303.64 | 315.76 | 327.88 | 340 | 353.7267 | 364.6067 | 375.4867 | 386.8267 | 396.7
N-0 | 1755.4513 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5542 | 551.7973 | 682.0405 | 812.2837 | 942.5269 | 1072.7701 | 1295.7542 | 1519.911 | 1744.0677 | 1967.4284 | 2189.5733
N-0 | 22.4262 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1075 | 6.9712 | 7.8349 | 8.6986 | 9.5623 | 10.426 | 11.3758 | 12.3433 | 13.3109 | 14.2525 | 15.1344
N-0 | 278.5405 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 68 | 73.6 | 79.2 | 84.8 | 90.4 | 96 | 104.6667 | 111.6667 | 118.6667 | 125.8667 | 132
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 4169341.4802 | 2664.1723 | 6696.6565 | 15296.142 | 23895.6274 | 32495.1129 | 41094.5983 | 49694.0838 | 58293.5692 | 105854.9234 | 153416.2776 | 200977.6318 | 248538.986 | 358519.467 | 487919.1763 | 617318.8856 | 746718.595 | 876118.3043 | 1005518.0136 | 1321103.1152 | 1636688.2167 | 1952273.3183 | 2267858.4198 | 2583443.5214 | 3006340.4357 | 3429237.3501 | 3852134.2645 | 4275031.1789 | 4697928.0933
Commerical(N-1) | EENS | 17261683.4396 | 11054.9454 | 27787.6812 | 63471.1243 | 99154.5673 | 134838.0103 | 170521.4534 | 206204.8964 | 241888.3395 | 439243.5047 | 636598.6698 | 833953.835 | 1031309.0002 | 1437138.4913 | 1984187.3427 | 2531236.194 | 3078285.0454 | 3625333.8968 | 4172382.7482 | 5481898.6549 | 6791414.5616 | 8100930.4683 | 9410446.375 | 10719962.2818 | 12474767.0351 | 14229571.7884 | 15984376.5417 | 17739181.2951 | 19493986.0484
Aggregate | EENS | 21431024.9197 | 13719.1178 | 34484.3377 | 78767.2662 | 123050.1947 | 167333.1232 | 211616.0517 | 255898.9802 | 300181.9087 | 545098.4281 | 790014.9475 | 1034931.4668 | 1279847.9862 | 1795657.9583 | 2472106.519 | 3148555.0797 | 3825003.6404 | 4501452.2011 | 5177900.7618 | 6803001.7701 | 8428102.7783 | 10053203.7866 | 11678304.7949 | 13303405.8031 | 15481107.4708 | 17658809.1385 | 19836510.8062 | 22014212.474 | 24191914.1417
Residential (N-0) | EENS | 122110315.3067 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17866466.9567 | 20996797.7861 | 24698098.9882 | 28840317.3417 | 33531790.6692 | 38427795.4237 | 44456017.5812 | 49918498.143 | 55820183.6477 | 61722877.6256 | 67876114.3091 | 75348836.8647 | 83556334.3634 | 89719373.4245 | 99316519.1786
Commerical(N-0) | EENS | 523275410.8771 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 77675195.1106 | 90392543.5661 | 106694968.7558 | 124345366.1109 | 143659312.5749 | 164314472.8961 | 190301096.757 | 210956908.58 | 236555531.4522 | 259941794.1871 | 283902347.3383 | 314427814.4115 | 349006430.9324 | 369343245.2284 | 402405364.6952
Aggregate | EENS | 645385726.1838 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 95541662.0673 | 111389341.3522 | 131393067.744 | 153185683.4525 | 177191103.2441 | 202742268.3197 | 234757114.3382 | 260875406.723 | 292375715.1 | 321664671.8127 | 351778461.6473 | 389776651.2762 | 432562765.2958 | 459062618.6529 | 501721883.8738
Residential (N-1) | Value for Flex-1 | 1642693710.1654 | 24962423.7752 | 38784191.367 | 53281445.8236 | 68479322.8835 | 84403792.8927 | 101081686.8255 | 118540723.0844 | 136809535.102 | 155917699.7686 | 175895766.709 | 196775288.4342 | 218588851.3913 | 241370107.9411 | 265153809.2862 | 289975839.3812 | 315873249.8501 | 342884295.9428 | 371048473.5589 | 400406557.371 | 431000640.0776 | 462874172.8212 | 496072006.802 | 530640436.1238 | 566627241.9074 | 604081737.7076 | 643054816.2717 | 683598997.6779 | 725768478.8942
Commerical(N-1) | Value for Flex-1 | 6767294419.7288 | 102836012.6244 | 159776615.8034 | 219499976.6336 | 282109645.1203 | 347712609.546 | 416419403.6648 | 488344217.1086 | 563605009.0972 | 642323625.5496 | 724625919.6939 | 810641876.2795 | 900505739.4946 | 994356144.6977 | 1092336254.0738 | 1194593896.3283 | 1301281710.5366 | 1412557294.2703 | 1528583356.1215 | 1649527872.7563 | 1775564250.6253 | 1906871492.4673 | 2043634368.7447 | 2186043594.1533 | 2334296009.3518 | 2488594768.0638 | 2649149529.7057 | 2816176657.6995 | 2989899423.637
Aggregate | Value for Flex-1 | 8409988129.8943 | 127798436.3995 | 198560807.1705 | 272781422.4572 | 350588968.0038 | 432116402.4387 | 517501090.4903 | 606884940.193 | 700414544.1993 | 798241325.3182 | 900521686.403 | 1007417164.7137 | 1119094590.8859 | 1235726252.6388 | 1357490063.36 | 1484569735.7094 | 1617154960.3867 | 1755441590.213 | 1899631829.6804 | 2049934430.1273 | 2206564890.7029 | 2369745665.2885 | 2539706375.5468 | 2716684030.2771 | 2900923251.2592 | 3092676505.7715 | 3292204345.9773 | 3499775655.3774 | 3715667902.5312
Residential (N-1) | Value for Flex-2-1 | 77287537.7207 | 6206899.9199 | 6450518.2423 | 6701145.5758 | 6922702.9859 | 7150750.3027 | 7385131.9913 | 7631326.5061 | 7884163.7337 | 8144428.6706 | 8412502.1707 | 8690118.0978 | 8975605.8826 | 9269823.5621 | 9572275.1132 | 9881533.2135 | 10199762.8498 | 10527716.5867 | 10864924.2138 | 11206309.3507 | 11557276.2014 | 11918264.8351 | 12289202.1578 | 12663092.8617 | 13047018.3714 | 13441793.5024 | 13848404.766 | 14255560.9664 | 14674245.2186
Commerical(N-1) | Value for Flex-2-1 | 348385320.4578 | 27978544.5546 | 29076691.1617 | 30206431.9514 | 31205135.644 | 32233093.5776 | 33289604.6542 | 34399363.8398 | 35539066.0631 | 36712249.8146 | 37920631.851 | 39172027.8275 | 40458907.3988 | 41785138.2968 | 43148484.6221 | 44542512.5024 | 45976980.9445 | 47455282.2475 | 48975296.8667 | 50514142.2464 | 52096178.6568 | 53723389.7771 | 55395446.1248 | 57080815.2866 | 58811417.8608 | 60590926.7519 | 62423788.8089 | 64259107.2511 | 66146390.1391
Aggregate of Flex-2 (Component 1) | Value for Flex-2-1 | 425672858.1785 | 34185444.4744 | 35527209.404 | 36907577.5272 | 38127838.6299 | 39383843.8803 | 40674736.6455 | 42030690.3459 | 43423229.7968 | 44856678.4852 | 46333134.0216 | 47862145.9253 | 49434513.2815 | 51054961.8589 | 52720759.7352 | 54424045.7159 | 56176743.7943 | 57982998.8342 | 59840221.0805 | 61720451.5971 | 63653454.8583 | 65641654.6122 | 67684648.2827 | 69743908.1483 | 71858436.2322 | 74032720.2544 | 76272193.5749 | 78514668.2175 | 80820635.3577
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 330880723.2643 | 16525778.9479 | 18692353.6673 | 20973438.9271 | 22643631.9924 | 24492440.8648 | 26312589.4039 | 28198232.638 | 30389934.5969 | 32668876.4373 | 35031087.5617 | 37829419.2372 | 40460383.2999 | 43328283.1641 | 46384661.8653 | 49426886.0569 | 52788925.4165 | 56250107.5346 | 59922389.5591 | 63534752.4512 | 67372879.8267 | 71215457.8081 | 75184124.4931 | 79423008.2209 | 83735520.2549 | 88059787.8326 | 92691191.644 | 96907380.4087 | 101570342.7899
Aggregate ($M) |  | 9833.3585 | 180461918.982 | 257908700.4243 | 338482348.7105 | 422285250.5472 | 509142280.2958 | 599331743.7398 | 696898453.1798 | 798675594.8827 | 906667032.0724 | 1023021295.7321 | 1147090264.4137 | 1278610158.568 | 1415889563.6474 | 1554609253.5469 | 1702958563.9141 | 1861338700.9819 | 2027361832.2355 | 2201763444.3258 | 2384734904.2653 | 2580776442.5044 | 2777531388.2184 | 2986629168.2174 | 3200819024.2621 | 3423776776.8644 | 3662204474.2732 | 3913567007.2984 | 4156274535.1304 | 4423972678.6943
Aggregate ($M)+ Monetized Losses |  | 9838.7312 | 180827028.982 | 258289908.4154 | 338885360.1696 | 422710917.3926 | 509591483.4147 | 599805393.904 | 697397491.9898 | 799200995.7393 | 907219801.1787 | 1023602473.125 | 1147700925.0269 | 1279251413.3267 | 1416562560.5958 | 1555315179.0104 | 1703698643.6953 | 1862114201.5934 | 2028174062.1688 | 2202613755.3593 | 2385624692.8101 | 2581707150.9917 | 2778504506.5276 | 2987646235.1467 | 3201881629.0436 | 3424886560.7238 | 3663363132.0365 | 3914776289.0458 | 4157536247.9001 | 4425288688.2363
Project Cost |  | 545
Benefit-Cost Ratio |  | 18.0527

## SDG&E
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| SDG&E | Losses (MWh) | 44182.4 | 44715.005 | 45093.4314 | 45471.8578 | 45850.2842 | 46228.7106 | 46607.137 | 46985.5634 | 47363.9897 | 47742.4161 | 48120.8425 | 48499.2689 | 48877.6953 | 49256.1217 | 49634.5481 | 50012.9745 | 50391.4009 | 50769.8273 | 51148.2537 | 51526.6801 | 51905.1064 | 52283.5328 | 52661.9592 | 53040.3856 | 53418.812 | 53797.2384 | 54175.6648 | 54554.0912
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.4 | 63.56 | 96.72 | 129.88 | 163.04 | 196.2
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 9.34 | 11.58 | 13.82 | 16.06 | 18.3
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25124 | 1.1519 | 2.0526 | 2.9532 | 3.8539 | 4.7545
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031405 | 0.065579 | 0.099753 | 0.13393 | 0.1681 | 0.20227
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4.8 | 5.6 | 6.4 | 7.2 | 8
N-1 |  | Deficit Flex-1 | 3717.6324 | 5825.0395 | 7735.3222 | 9645.6049 | 11555.8876 | 13466.1703 | 15376.4529 | 17286.7356 | 19197.0183 | 21107.301 | 23017.5837 | 24927.8664 | 26838.1491 | 28748.4317 | 30658.7144 | 32568.9971 | 34479.2798 | 36389.5625 | 38299.8452 | 40210.1279 | 42120.4105 | 44030.6932 | 45940.9759 | 47851.2586 | 49761.5413 | 51671.824 | 53582.1067 | 55492.3894
N-1 |  | Deficit Flex-2-1 | 58391.3519 | 60909.1505 | 63468.7534 | 65012.9523 | 66580.8234 | 68152.8622 | 69883.551 | 71621.9247 | 73383.2755 | 75162.7501 | 76998.3621 | 78847.7006 | 80725.5882 | 82598.7507 | 84416.5313 | 86236.7121 | 88071.4543 | 89891.6351 | 91580.7628 | 93269.8906 | 94959.0183 | 96633.5846 | 98133.4135 | 99618.681 | 101103.9485 | 102603.7775 | 103870.6233 | 105137.4691
|  | Deficit Flex-2-2 | 13056.4521 | 15232.4908 | 17633.376 | 19168.7768 | 20799.3444 | 22493.1163 | 24426.8606 | 26412.5649 | 28514.2344 | 30698.9165 | 33011.4003 | 35402.8386 | 37912.6384 | 40486.0614 | 43070.2782 | 45740.9464 | 48535.5399 | 51366.9248 | 54079.3348 | 56880.8612 | 59780.9796 | 62754.8593 | 65514.9882 | 68308.008 | 71171.9171 | 74111.9028 | 76647.2242 | 79230.1966
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 62.75 | 108.3 | 153.85 | 199.4 | 290.52 | 381.64 | 472.76 | 563.88 | 655 | 823.8 | 992.6 | 1161.4 | 1330.2 | 1499
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 26.95 | 36.7 | 46.45 | 56.2 | 67.4 | 78.6 | 89.8 | 101 | 112.2 | 120.16 | 128.12 | 136.08 | 144.04 | 152
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0299 | 0.28239 | 0.53489 | 0.78738 | 1.0399 | 2.1982 | 3.3566 | 4.515 | 5.6733 | 6.8317 | 12.7615 | 18.6914 | 24.6212 | 30.5511 | 36.4809
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01495 | 0.054541 | 0.094131 | 0.13372 | 0.17331 | 0.25251 | 0.33171 | 0.41091 | 0.49011 | 0.56931 | 0.71602 | 0.86274 | 1.0095 | 1.1562 | 1.3029
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.25 | 3.5 | 4.75 | 6 | 7.2 | 8.4 | 9.6 | 10.8 | 12 | 15.2 | 18.4 | 21.6 | 24.8 | 28
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189312.7175 | 417945.4012 | 899616.2046 | 1360534.7336 | 1635951.6139 | 2351803.3341 | 3092388.1831 | 3700393.0013 | 4245985.7717 | 5216393.2431 | 6359347.1759 | 7431686.7425 | 9110207.6789 | 10293767.4071 | 12430871.0299
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066768.5672 | 2178110.4173 | 4775582.9478 | 7115478.6313 | 7707603.585 | 11301152.0514 | 15049706.9123 | 17263890.5757 | 18687227.3389 | 23201983.167 | 28255550.6437 | 32098928.0785 | 39267846.772 | 44561298.2496 | 54181886.9572
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38709.1648 | 74879.6548 | 111050.1448 | 147220.6349 | 183391.1249 | 219561.615
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160623.1306 | 310712.0665 | 460801.0023 | 610889.9382 | 760978.8741 | 911067.8099
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 3966989.8423 | 4707050.0965 | 5543241.2374 | 6095692.5942 | 6811876.7156 | 7457565.859 | 8272370.8013 | 9159673.3031 | 9932379.814 | 10912742.266 | 12065920.7978 | 13154935.4186 | 14285891.8348 | 15646720.8149 | 16958054.5979 | 18437737.9304 | 19885747.6023 | 21543950.1016 | 22934221.0592 | 24739465.7472 | 26598021.7553 | 28551363.1429 | 30544623.6672 | 32507953.7789 | 34666804.7919 | 36919934.8775 | 39084466.9122 | 41306551.6444
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 71431.0415 | Losses (MWh) | 5899.35 | 6173.045 | 6391.1225 | 6609.1999 | 6827.2774 | 7045.3548 | 7263.4323 | 7481.5097 | 7699.5872 | 7917.6646 | 8135.7421 | 8353.8195 | 8571.897 | 8789.9745 | 9008.0519 | 9226.1294 | 9444.2068 | 9662.2843 | 9880.3617 | 10098.4392 | 10316.5166 | 10534.5941 | 10752.6715 | 10970.749 | 11188.8265 | 11406.9039 | 11624.9814 | 11843.0588
| 3652887.0567 | Losses ($) | 235974 | 253094.845 | 268586.9211 | 284695.4168 | 301441.4705 | 318846.8921 | 336934.184 | 355726.5611 | 375247.9732 | 395523.1269 | 416577.5082 | 438437.4066 | 461129.939 | 484683.0747 | 509125.6609 | 534487.4496 | 560799.1241 | 588092.3276 | 616399.692 | 645754.8668 | 676192.5505 | 707748.5217 | 740459.671 | 774364.035 | 809500.83 | 845910.4871 | 883634.6891 | 922716.4071
N-1 | 9597.8795 | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5232.3 | 5993.72 | 6755.14 | 7516.56 | 8277.98 | 9039.4
N-1 | 259.4767 | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 64.3 | 73.46 | 82.62 | 91.78 | 100.94 | 110.1
N-1 | 1136.4404 | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 737.8883 | 976.205 | 1214.5216 | 1452.8383 | 1691.1549 | 1929.4716
N-1 | 8.4508 | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.7486 | 5.448 | 6.1474 | 6.8468 | 7.5463 | 8.2457
N-1 | 700.5517 | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 200 | 210.6 | 221.2 | 231.8 | 242.4 | 253
N-1 | 122295.4802 | Flex-1 | 2609.4016 | 3765.5276 | 5118.7781 | 6472.0286 | 7825.2791 | 9178.5296 | 10531.7801 | 11885.0305 | 13238.281 | 14591.5315 | 15944.782 | 17298.0325 | 18651.283 | 20004.5335 | 21357.7839 | 22711.0344 | 24064.2849 | 25417.5354 | 26770.7859 | 28124.0364 | 29477.2869 | 30830.5373 | 32183.7878 | 33537.0383 | 34890.2888 | 36243.5393 | 37596.7898 | 38950.0403
N-1 | 1302863.5904 | Flex-2-1 | 136221.1839 | 137060.5368 | 137858.0854 | 138307.7277 | 138750.7392 | 139172.5416 | 139606.1077 | 140014.9477 | 140400.8105 | 140768.5495 | 141131.2753 | 141480.2745 | 141817.766 | 142142.9414 | 142455.3329 | 142765.3244 | 143077.7958 | 143387.7873 | 143675.4594 | 143963.1315 | 144250.8036 | 144535.9957 | 144791.4287 | 145044.3818 | 145297.3348 | 145552.7678 | 145768.5219 | 145984.2759
N-2 | 691817.7936 | Flex-2-2 | 47957.5128 | 52277.7891 | 56744.1988 | 59449.4493 | 62189.6372 | 64896.287 | 67894.4551 | 70947.9633 | 74044.1199 | 77204.0826 | 80498.882 | 83812.706 | 87190.6802 | 90575.5919 | 93857.1 | 97187.5228 | 100560.6899 | 103988.9587 | 107208.3859 | 110449.6902 | 113704.4519 | 116982.7062 | 119882.9434 | 122752.8815 | 125633.318 | 128574.7281 | 131079.6148 | 133592.5317
N-0 | 20285.7425 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3405.8667 | 3939.7 | 4473.5333 | 5007.3667 | 5541.2 | 6279.48 | 7017.76 | 7756.04 | 8494.32 | 9232.6 | 9990.76 | 10748.92 | 11507.08 | 12265.24 | 13023.4
N-0 | 1180.6909 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 202.8 | 208.05 | 213.3 | 218.55 | 223.8 | 226.28 | 228.76 | 231.24 | 233.72 | 236.2 | 240.68 | 245.16 | 249.64 | 254.12 | 258.6
N-0 | 1743.4027 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9319 | 255.0785 | 310.2251 | 365.3718 | 420.5184 | 549.7189 | 678.9194 | 808.1198 | 937.3203 | 1066.5207 | 1284.8633 | 1503.2059 | 1721.5484 | 1939.891 | 2158.2336
N-0 | 21.7647 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6281 | 4.2051 | 4.7822 | 5.3592 | 5.9362 | 6.7397 | 7.5432 | 8.3467 | 9.1502 | 9.9538 | 10.7936 | 11.6334 | 12.4732 | 13.313 | 14.1528
N-0 | 265.5136 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 46.6667 | 50.75 | 54.8333 | 58.9167 | 63 | 68.4 | 73.8 | 79.2 | 84.6 | 90 | 94.8 | 99.6 | 104.4 | 109.2 | 114
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 4588261.7197 | 2664.1723 | 6696.6565 | 15296.142 | 23895.6274 | 32495.1129 | 41094.5983 | 49694.0838 | 58293.5692 | 105854.9234 | 153416.2776 | 200977.6318 | 248538.986 | 392537.6555 | 536536.325 | 680534.9945 | 824533.664 | 968532.3336 | 1112531.0031 | 1456952.4967 | 1801373.9903 | 2145795.484 | 2490216.9776 | 2795929.3065 | 3313660.6152 | 3831391.924 | 4349123.2328 | 4866854.5416 | 5384585.8503
Commerical(N-1) | EENS | 19038926.9853 | 11054.9454 | 27787.6812 | 63471.1243 | 99154.5673 | 134838.0103 | 170521.4534 | 206204.8964 | 241888.3395 | 439243.5047 | 636598.6698 | 833953.835 | 1031309.0002 | 1628829.4388 | 2226349.8773 | 2823870.3159 | 3421390.7544 | 4018911.193 | 4616431.6315 | 6045603.7385 | 7474775.8455 | 8903947.9525 | 10333120.0595 | 11601669.0359 | 13749987.7649 | 15898306.4938 | 18046625.2228 | 20194943.9517 | 22343262.6806
Aggregate | EENS | 23627188.705 | 13719.1178 | 34484.3377 | 78767.2662 | 123050.1947 | 167333.1232 | 211616.0517 | 255898.9802 | 300181.9087 | 545098.4281 | 790014.9475 | 1034931.4668 | 1279847.9862 | 2021367.0943 | 2762886.2023 | 3504405.3104 | 4245924.4184 | 4987443.5265 | 5728962.6346 | 7502556.2352 | 9276149.8359 | 11049743.4365 | 12823337.0371 | 14397598.3424 | 17063648.3801 | 19729698.4178 | 22395748.4555 | 25061798.4932 | 27727848.531
Residential (N-0) | EENS | 115301754.5225 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17677154.2392 | 20578852.3848 | 23798482.7836 | 27479782.6081 | 31905265.7394 | 36119270.7938 | 41445707.3141 | 46364754.4531 | 51781625.4468 | 56736623.6839 | 61832729.3168 | 68321889.3123 | 74962689.0964 | 80002387.3281 | 87510450.8956
Commerical(N-0) | EENS | 492467659.2204 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 76608426.5434 | 88214433.1489 | 101919385.808 | 117229887.4796 | 136004827.9269 | 153257194.3781 | 175682796.4575 | 194472605.1805 | 218953642.952 | 237822300.2654 | 257155278.0414 | 284290384.2734 | 312258972.6953 | 327474882.117 | 350971098.6048
Aggregate | EENS | 607769413.7429 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 94285580.7826 | 108793285.5337 | 125717868.5916 | 144709670.0876 | 167910093.6664 | 189376465.1718 | 217128503.7716 | 240837359.6336 | 270735268.3988 | 294558923.9493 | 318988007.3582 | 352612273.5857 | 387221661.7917 | 407477269.4451 | 438481549.5004
Residential (N-1) | Value for Flex-1 | 672287712.2723 | 10295027.5105 | 15227769.3328 | 21217813.1654 | 27497841.8337 | 34078610.8023 | 40971232.0681 | 48187185.2655 | 55738329.1027 | 63636913.141 | 71895589.9255 | 80527427.4785 | 89545922.1655 | 98965011.9446 | 108799090.0114 | 119063018.849 | 129772144.6972 | 140942312.4511 | 152589881.0022 | 164731739.0356 | 177385321.295 | 190568625.3305 | 204300228.742 | 218599306.9332 | 233485651.3911 | 248979688.5049 | 265102498.9424 | 281875837.5964 | 299322154.1213
Commerical(N-1) | Value for Flex-1 | 2769578318.5621 | 42411730.0697 | 62732813.6664 | 87409593.0022 | 113281003.2963 | 140391353.1095 | 168786419.7862 | 198513495.2011 | 229621432.8744 | 262160696.4968 | 296183409.9048 | 331743408.5479 | 368896292.492 | 407699481.0029 | 448212268.7566 | 490495883.7223 | 534613546.7684 | 580630533.0394 | 628614235.1572 | 678634228.2978 | 730762337.1984 | 785072705.1514 | 841641865.0413 | 900548812.4849 | 961875081.1351 | 1025704820.21 | 1092124874.3129 | 1161224865.6084 | 1233097278.4221
Aggregate | Value for Flex-1 | 3441866030.8344 | 52706757.5802 | 77960582.9992 | 108627406.1676 | 140778845.13 | 174469963.9118 | 209757651.8544 | 246700680.4666 | 285359761.9771 | 325797609.6378 | 368078999.8303 | 412270836.0265 | 458442214.6575 | 506664492.9476 | 557011358.768 | 609558902.5713 | 664385691.4656 | 721572845.4905 | 781204116.1594 | 843365967.3334 | 908147658.4935 | 975641330.482 | 1045942093.7833 | 1119148119.4182 | 1195360732.5262 | 1274684508.715 | 1357227373.2553 | 1443100703.2048 | 1532419432.5434
Residential (N-1) | Value for Flex-2 | 53721266.0105 | 4535568.7122 | 4677603.3727 | 4822442.6719 | 4959125.9963 | 5099385.7651 | 5242760.101 | 5390570.267 | 5541515.6043 | 5695706.9753 | 5853390.8489 | 6015185.4315 | 6180811.7053 | 6350444.4996 | 6524130.6326 | 6701930.6205 | 6884427.2906 | 7071982.6644 | 7264487.3985 | 7461038.3389 | 7662876.5216 | 7870143.4645 | 8082845.7721 | 8299558.5358 | 8521909.4536 | 8750190.6932 | 8984712.8831 | 9222981.7723 | 9467548.6604
Commerical(N-1) | Value for Flex-2 | 242156769.7251 | 20444765.1699 | 21085007.9849 | 21737893.1348 | 22354013.9892 | 22986256.2105 | 23632537.8157 | 24298814.5995 | 24979223.6439 | 25674264.6791 | 26385048.7001 | 27114362.3664 | 27860947.9631 | 28625593.5598 | 29408510.1968 | 30209970.6597 | 31032602.1312 | 31878036.4787 | 32745780.8198 | 33631764.05 | 34541580.3288 | 35475867.569 | 36434655.5419 | 37411521.2545 | 38413801.8037 | 39442814.1796 | 40499958.5875 | 41573991.8115 | 42676414.2226
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 295878035.7356 | 24980333.8822 | 25762611.3576 | 26560335.8067 | 27313139.9855 | 28085641.9756 | 28875297.9166 | 29689384.8666 | 30520739.2482 | 31369971.6544 | 32238439.549 | 33129547.798 | 34041759.6683 | 34976038.0594 | 35932640.8293 | 36911901.2802 | 37917029.4218 | 38950019.1431 | 40010268.2183 | 41092802.3889 | 42204456.8504 | 43346011.0334 | 44517501.314 | 45711079.7903 | 46935711.2573 | 48193004.8728 | 49484671.4706 | 50796973.5838 | 52143962.883
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 224072258.9458 | 12558789.1056 | 13985303.5709 | 15430197.6897 | 16547939.3982 | 17680564.1492 | 18855023.5449 | 19925861.8368 | 21230261.2938 | 22736496.6233 | 24118345.2956 | 25763498.4394 | 27305447.8813 | 29042391.3293 | 30748240.0953 | 32490302.5944 | 34399376.3299 | 36436611.2374 | 38458325.5086 | 40717373.8851 | 42789097.8511 | 44797526.4437 | 46830050.97 | 49122666.4272 | 51524823.8467 | 53732433.3449 | 56185975.7006 | 58293399.0812 | 60835870.7274
Aggregate ($M) |  | 4593.2129 | 92198139.7282 | 122836828.1102 | 158437849.463 | 195564736.4348 | 233385763.1486 | 272331300.516 | 316100517.1728 | 361558648.8088 | 410804229.7473 | 465571172.4209 | 525145416.8013 | 589410093.3078 | 656688697.4578 | 720740706.6775 | 791258797.29 | 866665890.2273 | 946656589.4851 | 1033311766.1873 | 1122055165.0144 | 1219545866.8024 | 1315671971.0292 | 1420848251.5033 | 1522938387.9275 | 1629872923.3685 | 1748951918.9362 | 1872515430.6738 | 1984730143.8082 | 2111608664.1852
Aggregate ($M)+ Monetized Losses |  | 4596.8658 | 92434113.7282 | 123089922.9552 | 158706436.3842 | 195849431.8516 | 233687204.619 | 272650147.4081 | 316437451.3568 | 361914375.3699 | 411179477.7205 | 465966695.5477 | 525561994.3095 | 589848530.7145 | 657149827.3968 | 721225389.7522 | 791767922.9509 | 867200377.6768 | 947217388.6091 | 1033899858.5149 | 1122671564.7064 | 1220191621.6692 | 1316348163.5798 | 1421556000.0249 | 1523678847.5985 | 1630647287.4036 | 1749761419.7661 | 1873361341.1609 | 1985613778.4972 | 2112531380.5923
Project Cost |  | 469
Benefit-Cost Ratio |  | 9.8014

## Valley S to Valley N to Vista
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Valley South to Valley North to Vista | Losses (MWh) | 49722.95 | 50479.4 | 51032.9519 | 51586.5038 | 52140.0558 | 52693.6077 | 53247.1596 | 53800.7115 | 54354.2635 | 54907.8154 | 55461.3673 | 56014.9192 | 56568.4712 | 57122.0231 | 57675.575 | 58229.1269 | 58782.6788 | 59336.2308 | 59889.7827 | 60443.3346 | 60996.8865 | 61550.4385 | 62103.9904 | 62657.5423 | 63211.0942 | 63764.6462 | 64318.1981 | 64871.75
N-1 |  | EENS | 12.4 | 31.9 | 62.6333 | 93.3667 | 124.1 | 154.8333 | 185.5667 | 216.3 | 328.58 | 440.86 | 553.14 | 665.42 | 777.7 | 1050.86 | 1324.02 | 1597.18 | 1870.34 | 2143.5 | 2618.12 | 3092.74 | 3567.36 | 4041.98 | 4516.6 | 5149.78 | 5782.96 | 6416.14 | 7049.32 | 7682.5
N-1 |  | IP | 5.9 | 10.3 | 13.3 | 16.3 | 19.3 | 22.3 | 25.3 | 28.3 | 31.04 | 33.78 | 36.52 | 39.26 | 42 | 45.18 | 48.36 | 51.54 | 54.72 | 57.9 | 61.76 | 65.62 | 69.48 | 73.34 | 77.2 | 88.76 | 100.32 | 111.88 | 123.44 | 135
N-1 |  | SAIDI | 0.045307 | 0.1457 | 0.86574 | 1.5858 | 2.3058 | 3.0259 | 3.7459 | 4.466 | 9.4602 | 14.4544 | 19.4486 | 24.4428 | 29.437 | 54.6278 | 79.8186 | 105.0094 | 130.2001 | 155.3909 | 225.1752 | 294.9596 | 364.7439 | 434.5282 | 504.3125 | 637.5894 | 770.8663 | 904.1432 | 1037.4201 | 1170.697
N-1 |  | SAIFI | 0.011327 | 0.029139 | 0.057236 | 0.085333 | 0.11343 | 0.14153 | 0.16962 | 0.19772 | 0.30223 | 0.40674 | 0.51126 | 0.61577 | 0.72028 | 0.97704 | 1.2338 | 1.4905 | 1.7473 | 2.0041 | 2.4538 | 2.9035 | 3.3532 | 3.803 | 4.2527 | 4.8525 | 5.4524 | 6.0522 | 6.652 | 7.2519
N-1 |  | PFD | 4 | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 27.2 | 31.4 | 35.6 | 39.8 | 44 | 52.6 | 61.2 | 69.8 | 78.4 | 87 | 95.4 | 103.8 | 112.2 | 120.6 | 129 | 138.8 | 148.6 | 158.4 | 168.2 | 178
N-1 |  | Deficit Flex-1 | 4238.9824 | 6425.4824 | 8611.9824 | 10798.4824 | 12984.9824 | 15171.4824 | 17357.9824 | 19544.4824 | 21730.9824 | 23917.4824 | 26103.9824 | 28290.4824 | 30476.9824 | 32663.4824 | 34849.9824 | 37036.4824 | 39222.9825 | 41409.4825 | 43595.9825 | 45782.4825 | 47968.9825 | 50155.4825 | 52341.9825 | 54528.4825 | 56714.9825 | 58901.4825 | 61087.9825 | 63274.4825
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 17164.3208 | 19844.0887 | 22754.5274 | 24601.2435 | 26524.5104 | 28541.0948 | 30814.4348 | 33148.2171 | 35561.9498 | 38077.7187 | 40736.7643 | 43501.2116 | 46385.9444 | 49358.9359 | 52298.7216 | 55356.3439 | 58553.2882 | 61842.499 | 65024.8853 | 68293.2688 | 71656.491 | 75060.9515 | 78184.8129 | 81331.7015 | 84513.9878 | 87765.4351 | 90580.7698 | 93440.6833
N-0 |  | EENS(Valley South) | 2036: 4.8; 2037: 42.15; 2038: 79.5; 2039: 149; 2040: 218.5; 2041: 288; 2042: 357.5; 2043: 427; 2044: 542.18; 2045: 657.36; 2046: 772.54; 2047: 887.72; 2048: 1002.9
N-0 |  | EENS(Valley North) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4 | 181.3 | 346.2 | 511.1 | 676 | 1223.92 | 1771.84 | 2319.76 | 2867.68 | 3415.6 | 4332.48 | 5249.36 | 6166.24 | 7083.12 | 8000
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4 | 40.25 | 64.1 | 87.95 | 111.8 | 138.68 | 165.56 | 192.44 | 219.32 | 246.2 | 269.88 | 293.56 | 317.24 | 340.92 | 364.6
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014254 | 2.6115 | 5.2087 | 7.8059 | 10.4031 | 44.0218 | 77.6405 | 111.2592 | 144.8778 | 178.4965 | 300.7568 | 423.0171 | 545.2773 | 667.5376 | 789.7979
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014254 | 0.17486 | 0.33546 | 0.49606 | 0.65666 | 1.1933 | 1.7299 | 2.2666 | 2.8032 | 3.3399 | 4.324 | 5.3081 | 6.2922 | 7.2763 | 8.2604
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6.5 | 12 | 17.5 | 23 | 31.6 | 40.2 | 48.8 | 57.4 | 66 | 76.6 | 87.2 | 97.8 | 108.4 | 119
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170520.8073 | 778286.2861 | 1489424.024 | 3008537.6908 | 4687046.3501 | 7324251.2998 | 10234874.6628 | 13943843.6217 | 19386984.8463 | 24878781.6555 | 31065447.3938 | 36803118.4084 | 45397659.1559 | 53235106.7347 | 62235436.2505
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020123.7736 | 4440974.2644 | 7416212.0016 | 14147820.4726 | 21183859.8833 | 33747958.0049 | 46074334.1664 | 62171517.5212 | 87009946.6702 | 111032769.7665 | 137102438.2526 | 156116859.0978 | 192734521.1048 | 226650085.0329 | 262136710.198
N-1 Monetized | Residential | $ | 2647.9026 | 10044.4024 | 17440.9022 | 24837.402 | 32233.9018 | 39630.4016 | 47026.9014 | 54423.4012 | 95034.2273 | 135645.0533 | 176255.8794 | 216866.7054 | 257477.5314 | 381974.2392 | 506470.9469 | 630967.6546 | 755464.3623 | 879961.07 | 1146479.2724 | 1412997.4748 | 1679515.6772 | 1946033.8796 | 2212552.082 | 2636500.642 | 3060449.2021 | 3484397.7621 | 3908346.3221 | 4332294.8821
N-1 Monetized | Commercial | $ | 10987.4343 | 41676.7166 | 72365.9989 | 103055.2813 | 133744.5636 | 164433.8459 | 195123.1283 | 225812.4106 | 394329.8021 | 562847.1935 | 731364.585 | 899881.9765 | 1068399.368 | 1584996.6924 | 2101594.0168 | 2618191.3412 | 3134788.6657 | 3651385.9901 | 4757299.4941 | 5863212.9981 | 6969126.5022 | 8075040.0062 | 9180953.5102 | 10940122.0522 | 12699290.5941 | 14458459.1361 | 16217627.6781 | 17976796.22
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5110374.2214 | 6015097.5811 | 6967510.5921 | 7745187.9968 | 8491036.7137 | 9233048.7464 | 10172667.8173 | 11216525.0586 | 12260160.0595 | 13330830.0069 | 14604368.7155 | 15898045.9904 | 17328004.7347 | 18766389.6983 | 20232001.0865 | 21817429.4974 | 23600568.0435 | 25503802.0729 | 27434997.0562 | 29443388.6443 | 31566313.1487 | 33843442.2534 | 36000441.2918 | 38358137.1162 | 40806428.0067 | 43292848.4471 | 45372446.2399 | 47951699.3087
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 6560.5113 | Losses (MWh) | 358.8 | 408.65 | 451.6019 | 494.5538 | 537.5058 | 580.4577 | 623.4096 | 666.3615 | 709.3135 | 752.2654 | 795.2173 | 838.1692 | 881.1212 | 924.0731 | 967.025 | 1009.9769 | 1052.9288 | 1095.8808 | 1138.8327 | 1181.7846 | 1224.7365 | 1267.6885 | 1310.6404 | 1353.5923 | 1396.5442 | 1439.4962 | 1482.4481 | 1525.4
| 348715.3314 | Losses ($) | 14352 | 16754.65 | 18978.5708 | 21303.216 | 23732.2319 | 26269.384 | 28918.5611 | 31683.7787 | 34569.1831 | 37579.0553 | 40717.8154 | 43990.0266 | 47400.3997 | 50953.7977 | 54655.2404 | 58509.909 | 62523.1516 | 66700.4876 | 71047.6135 | 75570.4078 | 80274.9371 | 85167.4613 | 90254.4399 | 95542.5378 | 101038.6316 | 106749.816 | 112683.4104 | 118846.9659
N-1 | 1471.0441 | EENS | 5.6 | 8.1 | 9.2 | 10.3 | 11.4 | 12.5 | 13.6 | 14.7 | 19.52 | 24.34 | 29.16 | 33.98 | 210.95 | 227.04 | 243.13 | 259.22 | 275.31 | 291.4 | 496.85 | 702.3 | 907.75 | 1113.2 | 746.1 | 907.5 | 1068.9 | 1230.3 | 1391.7 | 1553.1
N-1 | -32.719 | IP | -2.4 | -4.3 | -4.4167 | -4.5333 | -4.65 | -4.7667 | -4.8833 | -5 | -4.79 | -4.58 | -4.37 | -4.16 | -2.5 | -1.28 | -0.06 | 1.16 | 2.38 | 3.6 | 1.72 | -0.16 | -2.04 | -3.92 | -5.8 | -5.96 | -6.12 | -6.28 | -6.44 | -6.6
N-1 | 374.1303 | SAIDI | 0.15809 | 0.31035 | 0.26665 | 0.22296 | 0.17926 | 0.13557 | 0.091871 | 0.048175 | 0.29325 | 0.53833 | 0.78341 | 1.0285 | 24.6997 | 28.1744 | 31.6491 | 35.1238 | 38.5984 | 42.0731 | 80.4239 | 118.7747 | 157.1254 | 195.4762 | 233.827 | 339.7674 | 445.7078 | 551.6482 | 657.5886 | 763.529
N-1 | 0.84873 | SAIFI | 0.0026789 | 0.0017839 | 0.00035493 | -0.001074 | -0.0025029 | -0.0039318 | -0.0053607 | -0.0067897 | -0.0063576 | -0.0059256 | -0.0054935 | -0.0050615 | 0.15211 | 0.15705 | 0.16198 | 0.16691 | 0.17184 | 0.17678 | 0.24687 | 0.31697 | 0.38707 | 0.45717 | 0.52727 | 0.66104 | 0.79481 | 0.92857 | 1.0623 | 1.1961
N-1 | 364.9905 | PFD | 14 | 23 | 25.3333 | 27.6667 | 30 | 32.3333 | 34.6667 | 37 | 39.8 | 42.6 | 45.4 | 48.2 | 53.8333 | 55.0667 | 56.3 | 57.5333 | 58.7667 | 60 | 63 | 66 | 69 | 72 | 75 | 76.6 | 78.2 | 79.8 | 81.4 | 83
N-1 | 98755.5743 | Flex-1 | 2088.0515 | 3165.0847 | 4242.1179 | 5319.151 | 6396.1842 | 7473.2174 | 8550.2506 | 9627.2837 | 10704.3169 | 11781.3501 | 12858.3832 | 13935.4164 | 15012.4496 | 16089.4828 | 17166.5159 | 18243.5491 | 19320.5823 | 20397.6154 | 21474.6486 | 22551.6818 | 23628.7149 | 24705.7481 | 25782.7813 | 26859.8145 | 27936.8476 | 29013.8808 | 30090.914 | 31167.9471
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 625479.561 | Flex-2-2 | 43849.6441 | 47666.1912 | 51623.0473 | 54016.9826 | 56464.4711 | 58848.3085 | 61506.8809 | 64212.3112 | 66996.4044 | 69825.2804 | 72773.518 | 75714.333 | 78717.3741 | 81702.7173 | 84628.6566 | 87572.1253 | 90542.9416 | 93513.3844 | 96262.8354 | 99037.2825 | 101828.9405 | 104676.614 | 107213.1187 | 109729.1881 | 112291.2474 | 114921.1958 | 117146.0692 | 119382.045
N-0 | 16261.7414 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3406.6667 | 3821.15 | 4230.8333 | 4607.9667 | 4985.1 | 5197.08 | 5409.06 | 5621.04 | 5833.02 | 6045 | 5939.9 | 5834.8 | 5729.7 | 5624.6 | 5519.5
N-0 | 1010.1631 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 203.6 | 194.75 | 185.9 | 177.05 | 168.2 | 155 | 141.8 | 128.6 | 115.4 | 102.2 | 90.96 | 79.72 | 68.48 | 57.24 | 46
N-0 | 1459.115 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9475 | 252.7494 | 305.5513 | 358.3533 | 411.1552 | 507.8953 | 604.6355 | 701.3756 | 798.1158 | 894.8559 | 996.8681 | 1098.8802 | 1200.8923 | 1302.9045 | 1404.9166
N-0 | 18.1498 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6288 | 4.0848 | 4.5408 | 4.9969 | 5.4529 | 5.7989 | 6.145 | 6.4911 | 6.8371 | 7.1832 | 7.1856 | 7.1881 | 7.1905 | 7.1929 | 7.1954
N-0 | 199.6331 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 46.6667 | 46.5 | 46.3333 | 46.1667 | 46 | 44 | 42 | 40 | 38 | 36 | 33.4 | 30.8 | 28.2 | 25.6 | 23
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 1002742.6621 | 16.2698 | -3347.7459 | -2144.7603 | -941.7746 | 261.211 | 1464.1967 | 2667.1823 | 3870.168 | 10820.6961 | 17771.2243 | 24721.7524 | 31672.2806 | 135060.1241 | 154562.0859 | 174064.0476 | 193566.0094 | 213067.9712 | 232569.933 | 310473.2243 | 388376.5155 | 466279.8067 | 544183.098 | 622086.3892 | 752039.628 | 881992.8668 | 1011946.1056 | 1141899.3444 | 1271852.5832
Commerical(N-1) | EENS | 4160917.7071 | 67.5111 | -13889.0354 | -8894.8747 | -3900.714 | 1093.4467 | 6087.6075 | 11081.7682 | 16075.9289 | 44913.7026 | 73751.4763 | 102589.25 | 131427.0237 | 560430.0708 | 641353.1849 | 722276.299 | 803199.4132 | 884122.5273 | 965045.6414 | 1288304.2444 | 1611562.8474 | 1934821.4504 | 2258080.0534 | 2581338.6564 | 3120577.7792 | 3659816.902 | 4199056.0249 | 4738295.1477 | 5277534.2705
Aggregate | EENS | 5163660.3692 | 83.7809 | -17236.7813 | -11039.6349 | -4842.4886 | 1354.6578 | 7551.8042 | 13748.9505 | 19946.0969 | 55734.3987 | 91522.7006 | 127311.0025 | 163099.3043 | 695490.1949 | 795915.2708 | 896340.3467 | 996765.4226 | 1097190.4985 | 1197615.5744 | 1598777.4687 | 1999939.3629 | 2401101.2571 | 2802263.1513 | 3203425.0456 | 3872617.4072 | 4541809.7688 | 5211002.1305 | 5880194.4921 | 6549386.8537
Residential (N-0) | EENS | 91909509.0501 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17695946.1494 | 20218511.5 | 23208674.9643 | 25831779.6509 | 28854171.0032 | 31146822.8281 | 34303220.8344 | 36121303.8328 | 36640626.3722 | 37074235.2715 | 37126629.099 | 38950457.6464 | 38675237.6194 | 37061048.0006 | 37705885.675
Commerical(N-0) | EENS | 391312838.4354 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 76655071.337 | 85951569.3017 | 99278756.7542 | 110197545.6383 | 122528571.6287 | 130810388.4245 | 144658169.2034 | 149564978.235 | 150630923.6207 | 149991513.6659 | 148308390.4326 | 160272453.2541 | 158792298.3626 | 145386095.3337 | 143016275.3641
Aggregate | EENS | 483222347.4855 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 94351017.4864 | 106170080.8016 | 122487431.7184 | 136029325.2892 | 151382742.6319 | 161957211.2527 | 178961390.0378 | 185686282.0678 | 187271549.9929 | 187065748.9374 | 185435019.5316 | 199222910.9005 | 197467535.9819 | 182447143.3343 | 180722161.039
Residential (N-1) | Value for Flex-1 | 542122761.4057 | 8238114.0347 | 12799582.0479 | 17583974.6405 | 22599587.1239 | 27854990.2474 | 33359038.7851 | 39120880.3807 | 45149964.6569 | 51456052.5967 | 58049226.2056 | 64939898.462 | 72138823.5649 | 79657107.4864 | 87506218.8392 | 95698000.0675 | 104244678.9704 | 113158880.5684 | 122453639.322 | 132142411.7129 | 142239089.1988 | 152758011.5516 | 163713980.5914 | 175122274.3259 | 186998661.5092 | 199359416.6303 | 212221335.344 | 225601750.3579 | 239518547.788
Commerical(N-1) | Value for Flex-1 | 2233346554.7265 | 33938002.4352 | 52729574.3762 | 72439513.6626 | 93101993.9295 | 114752323.5136 | 137426980.8307 | 161163650.8115 | 186001262.4283 | 211980027.3442 | 239141479.7169 | 267528517.1911 | 297185443.1142 | 328158010.0103 | 360493464.3491 | 394240592.6487 | 429449768.948 | 466173003.6919 | 504463994.0674 | 544378175.8343 | 585972776.6933 | 629306871.2354 | 674441437.5191 | 721439415.3225 | 770365766.1176 | 821287534.8179 | 874273913.3493 | 929396306.0981 | 986728397.2885
Aggregate | Value for Flex-1 | 2775469316.1322 | 42176116.4699 | 65529156.424 | 90023488.3031 | 115701581.0534 | 142607313.761 | 170786019.6158 | 200284531.1923 | 231151227.0853 | 263436079.941 | 297190705.9225 | 332468415.6531 | 369324266.6791 | 407815117.4966 | 447999683.1883 | 489938592.7162 | 533694447.9184 | 579331884.2603 | 626917633.3894 | 676520587.5472 | 728211865.8921 | 782064882.787 | 838155418.1104 | 896561689.6483 | 957364427.6268 | 1020646951.4481 | 1086495248.6933 | 1154998056.4561 | 1226246945.0765
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1 and 2) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 201421523.7425 | 11415404.7265 | 12677256.0862 | 14005928.335 | 14898443.9956 | 16001404.1511 | 17079540.6575 | 18025564.8207 | 19173409.5383 | 20408716.3778 | 21700257.5548 | 23225050.5217 | 24562337.3095 | 26000278.4294 | 27628571.2119 | 29216356.1057 | 31019684.7629 | 32721790.7961 | 34498473.5373 | 36216597.8881 | 38085174.9541 | 39829235.0504 | 41537971.8595 | 43666848.8026 | 45674640.5094 | 47592810.1302 | 49813062.131 | 52005419.7536 | 54190723.0631
Aggregate ($M) |  | 3465.2768 | 55530145.0197 | 83283021.5737 | 111759519.536 | 141396944.2868 | 171592332.5587 | 202504823.2258 | 237852535.9862 | 274492287.1015 | 314255584.1211 | 359327858.9763 | 408767380.248 | 462390526.4076 | 518495294.1482 | 570775187.1574 | 626221369.9702 | 688198329.8223 | 749180190.8441 | 813996465.1329 | 876293174.1567 | 947258370.2469 | 1009981501.1622 | 1069767203.1142 | 1130497712.434 | 1192346705.075 | 1272004482.2476 | 1338986848.9367 | 1395330814.036 | 1467709216.0324
Aggregate ($M)+ Monetized Losses |  | 3465.6256 | 55544497.0197 | 83299776.2237 | 111778498.1068 | 141418247.5028 | 171616064.7906 | 202531092.6098 | 237881454.5473 | 274523970.8802 | 314290153.3042 | 359365438.0316 | 408808098.0634 | 462434516.4341 | 518542694.5479 | 570826140.9551 | 626276025.2106 | 688256839.7314 | 749242713.9957 | 814063165.6206 | 876364221.7701 | 947333940.6547 | 1010061776.0993 | 1069852370.5755 | 1130587966.8739 | 1192442247.6128 | 1272105520.8792 | 1339093598.7527 | 1395443497.4464 | 1467828062.9983
Project Cost |  | 270
Benefit-Cost Ratio |  | 12.8357

## Centralized BESS in Valley S
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Centralized BESS in Valley South | Losses (MWh) | 48907.95 | 49635.9 | 50140.5981 | 50645.2962 | 51149.9942 | 51654.6923 | 52159.3904 | 52664.0885 | 53168.7865 | 53673.4846 | 54178.1827 | 54682.8808 | 55187.5788 | 55692.2769 | 56196.975 | 56701.6731 | 57206.3712 | 57711.0692 | 58215.7673 | 58720.4654 | 59225.1635 | 59729.8615 | 60234.5596 | 60739.2577 | 61243.9558 | 61748.6538 | 62253.3519 | 62758.05
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.16 | 12.32 | 18.48 | 24.64 | 30.8
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.46 | 2.92 | 4.38 | 5.84 | 7.3
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14537 | 0.29074 | 0.4361 | 0.58147 | 0.72684
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014854 | 0.029707 | 0.044561 | 0.059415 | 0.074268
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 1.6 | 2.4 | 3.2 | 4
N-1 |  | Deficit Flex-1 | 4263.3321 | 6462.3918 | 8661.4515 | 10860.5112 | 13059.571 | 15258.6307 | 17457.6904 | 19656.7501 | 21855.8099 | 24054.8696 | 26253.9293 | 28452.989 | 30652.0488 | 32851.1085 | 35050.1682 | 37249.2279 | 39448.2877 | 41647.3474 | 43846.4071 | 46045.4668 | 48244.5266 | 50443.5863 | 52642.646 | 54841.7057 | 57040.7655 | 59239.8252 | 61438.8849 | 63637.9446
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 60963.4488 | 67379.7239 | 74131.6732 | 78284.4708 | 82555.9703 | 86840.9805 | 91614.7847 | 96459.1873 | 101387.7379 | 106407.8871 | 111665.5701 | 116974.1271 | 122422.6394 | 127910.5622 | 133267.8929 | 138688.4271 | 144199.2753 | 149725.2845 | 154923.9853 | 160186.9019 | 165528.5685 | 170942.2923 | 175812.4052 | 180641.2339 | 185516.7043 | 190462.6228 | 194677.705 | 198913.3277
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4490.4205 | 8980.841 | 13471.2614 | 17961.6819 | 22452.1024
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188877.2068 | 377754.4136 | 566631.6204 | 755508.8272 | 944386.034
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 16513545.6762 | 18660036.5024 | 20911156.9432 | 22556980.2 | 24377241.8671 | 26165895.5482 | 28004195.7517 | 30136343.7678 | 32330543.2104 | 34590850.2323 | 37271320.0598 | 39778867.0363 | 42493884.8302 | 45386907.6902 | 48245178.529 | 51407801.0694 | 54631111.1584 | 58004741.3279 | 61334544.1963 | 64867163.423 | 68356574.951 | 71956093.3357 | 75841194.2446 | 79766256.828 | 83688089.1618 | 87882969.4265 | 91720086.4401 | 95968685.8676
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 17572.5048 | Losses (MWh) | 1173.8 | 1252.15 | 1343.9558 | 1435.7615 | 1527.5673 | 1619.3731 | 1711.1788 | 1802.9846 | 1894.7904 | 1986.5962 | 2078.4019 | 2170.2077 | 2262.0135 | 2353.8192 | 2445.625 | 2537.4308 | 2629.2365 | 2721.0423 | 2812.8481 | 2904.6538 | 2996.4596 | 3088.2654 | 3180.0712 | 3271.8769 | 3363.6827 | 3455.4885 | 3547.2942 | 3639.1
| 920382.92 | Losses ($) | 46952 | 51338.15 | 56479.7412 | 61846.3256 | 67445.9394 | 73286.88 | 79377.7138 | 85727.2851 | 92344.7238 | 99239.4549 | 106421.2071 | 113900.0223 | 121686.265 | 129790.6323 | 138224.164 | 146998.2532 | 156124.6568 | 165615.5066 | 175483.321 | 185741.0164 | 196401.9195 | 207479.7797 | 218988.7816 | 230943.5588 | 243359.2069 | 256251.2976 | 269635.8934 | 283529.5619
N-1 | 9646.2651 | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6051.12 | 6839.54 | 7627.96 | 8416.38 | 9204.8
N-1 | 264.2033 | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 81.34 | 91.28 | 101.22 | 111.16 | 121.1
N-1 | 1137.4733 | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.2115 | 1216.2834 | 1455.3554 | 1694.4273 | 1933.4993
N-1 | 8.4905 | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.4987 | 6.2175 | 6.9362 | 7.655 | 8.3737
N-1 | 702.6918 | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 214.6 | 225.2 | 235.8 | 246.4 | 257
N-1 | 97603.9451 | Flex-1 | 2063.7019 | 3128.1754 | 4192.6488 | 5257.1223 | 6321.5957 | 7386.0691 | 8450.5426 | 9515.016 | 10579.4895 | 11643.9629 | 12708.4364 | 13772.9098 | 14837.3833 | 15901.8567 | 16966.3302 | 18030.8036 | 19095.2771 | 20159.7505 | 21224.2239 | 22288.6974 | 23353.1708 | 24417.6443 | 25482.1177 | 26546.5912 | 27611.0646 | 28675.5381 | 29740.0115 | 30804.485
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 20162.1209 | Flex-2-2 | 50.5161 | 130.5561 | 245.9015 | 333.7552 | 433.0113 | 548.4227 | 706.5309 | 901.3409 | 1170.6164 | 1495.112 | 1844.7122 | 2241.4175 | 2680.6791 | 3151.0911 | 3659.4852 | 4240.0421 | 4896.9545 | 5630.5989 | 6363.7354 | 7143.6495 | 7956.863 | 8795.2731 | 9585.5264 | 10419.6557 | 11288.5309 | 12224.0081 | 13049.1341 | 13909.4006
N-0 | 21183.8076 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 | 1335.7024 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 | 1756.8124 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 | 22.5453 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 | 284.3733 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 4646660.6957 | 2664.1723 | 6696.6565 | 15296.142 | 23895.6274 | 32495.1129 | 41094.5983 | 49694.0838 | 58293.5692 | 105854.9234 | 153416.2776 | 200977.6318 | 248538.986 | 392537.6555 | 536536.325 | 680534.9945 | 824533.664 | 968532.3336 | 1112531.0031 | 1456952.4967 | 1801373.9903 | 2145795.484 | 2490216.9776 | 2834638.4712 | 3384049.8496 | 3933461.2279 | 4482872.6062 | 5032283.9846 | 5581695.3629
Commerical(N-1) | EENS | 19078719.6649 | 11054.9454 | 27787.6812 | 63471.1243 | 99154.5673 | 134838.0103 | 170521.4534 | 206204.8964 | 241888.3395 | 439243.5047 | 636598.6698 | 833953.835 | 1031309.0002 | 1628829.4388 | 2226349.8773 | 2823870.3159 | 3421390.7544 | 4018911.193 | 4616431.6315 | 6045603.7385 | 7474775.8455 | 8903947.9525 | 10333120.0595 | 11762292.1666 | 13871822.6246 | 15981353.0826 | 18090883.5406 | 20200413.9986 | 22309944.4566
Aggregate | EENS | 23725380.3606 | 13719.1178 | 34484.3377 | 78767.2662 | 123050.1947 | 167333.1232 | 211616.0517 | 255898.9802 | 300181.9087 | 545098.4281 | 790014.9475 | 1034931.4668 | 1279847.9862 | 2021367.0943 | 2762886.2023 | 3504405.3104 | 4245924.4184 | 4987443.5265 | 5728962.6346 | 7502556.2352 | 9276149.8359 | 11049743.4365 | 12823337.0371 | 14596930.6378 | 17255872.4741 | 19914814.3105 | 22573756.1468 | 25232697.9832 | 27891639.8195
Residential (N-0) | EENS | 122402385.4505 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17866466.9567 | 20996797.7861 | 24698098.9882 | 28840317.3417 | 33541217.3533 | 38471074.1279 | 44538095.4972 | 50065147.4545 | 56027611.2185 | 61953016.927 | 68192076.4928 | 75753576.0548 | 84072896.7752 | 90296154.7352 | 99941321.9255
Commerical(N-0) | EENS | 524690134.185 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 77675195.1106 | 90392543.5661 | 106694968.7558 | 124345366.1109 | 143712431.512 | 164558346.4294 | 190732503.3698 | 211736495.7562 | 237640870.2909 | 261024283.4324 | 285410828.6852 | 316389312.3519 | 351526819.4674 | 372036180.3666 | 405152985.562
Aggregate | EENS | 647092519.6355 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 95541662.0673 | 111389341.3522 | 131393067.744 | 153185683.4525 | 177253648.8653 | 203029420.5574 | 235270598.867 | 261801643.2106 | 293668481.5094 | 322977300.3594 | 353602905.1779 | 392142888.4066 | 435599716.2426 | 462332335.1019 | 505094307.4875
Residential (N-1) | Value for Flex-1 | 535800846.0954 | 8142046.0166 | 12650320.8851 | 17378920.7183 | 22336044.0927 | 27530161.8103 | 32970025.3862 | 38664675.7897 | 44623452.4476 | 50856002.516 | 57372290.4301 | 64182607.7383 | 71297583.2304 | 78728193.3672 | 86485773.0214 | 94582026.5374 | 103029039.1211 | 111839288.5673 | 121025657.3365 | 130601444.9887 | 140580380.9878 | 150976637.8836 | 161804844.8861 | 173080101.8401 | 184817993.6138 | 197034604.9124 | 209746535.53 | 222970916.0504 | 236725424.0121
Commerical(N-1) | Value for Flex-1 | 2207302586.8604 | 33542237.5043 | 52114673.237 | 71594766.8579 | 92016293.489 | 113414149.7224 | 135824388.5841 | 159284255.5453 | 183832225.6116 | 209508041.5216 | 236352753.086 | 264408757.7027 | 293719842.0796 | 324331225.2018 | 356289602.5787 | 389643191.8088 | 424441779.4988 | 460736769.5783 | 498581233.0497 | 538029959.2136 | 579139508.4151 | 621968266.3522 | 666576499.9933 | 713026415.1501 | 761382215.7521 | 811710164.8748 | 864078647.5688 | 918558235.5445 | 975221753.7642
Aggregate | Value for Flex-1 | 2743103432.9559 | 41684283.5209 | 64764994.1221 | 88973687.5762 | 114352337.5817 | 140944311.5327 | 168794413.9703 | 197948931.335 | 228455678.0592 | 260364044.0376 | 293725043.5161 | 328591365.441 | 365017425.31 | 403059418.569 | 442775375.6001 | 484225218.3462 | 527470818.6198 | 572576058.1457 | 619606890.3862 | 668631404.2024 | 719719889.4029 | 772944904.2358 | 828381344.8795 | 886106516.9902 | 946200209.3659 | 1008744769.7872 | 1073825183.0988 | 1141529151.5949 | 1211947177.7763
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 7241189.2668 | 12233.2716 | 32317.1649 | 62281.9839 | 86651.7925 | 115198.9977 | 146693.8557 | 194036.8864 | 253590.8291 | 338333.2269 | 440237.3294 | 558099.1774 | 681516.2636 | 834398.3339 | 1008053.2199 | 1203178.6633 | 1429313.191 | 1691247.6813 | 1997534.2823 | 2317050.748 | 2661400.1753 | 3038973.2481 | 3425320.7772 | 3826095.8499 | 4266520.7975 | 4711148.9751 | 5222941.1516 | 5657779.5534 | 6173736.5042
Aggregate ($M) |  | 3421.1625 | 43648775.9528 | 69925641.4695 | 96855879.3591 | 125363801.2952 | 154209103.6424 | 183784435.026 | 217927558.2243 | 253157155.178 | 291602529.0962 | 335300668.5913 | 383130999.156 | 435319612.6743 | 489899592.0244 | 542087977.0897 | 600322143.672 | 664539123.9732 | 732440432.806 | 804587036.1683 | 881480431.7429 | 966928038.2811 | 1048835264.131 | 1138298484.2032 | 1227506843.8372 | 1321325507.8155 | 1425513621.4795 | 1537221596.6398 | 1634751964.2333 | 1751106861.5875
Aggregate ($M)+ Monetized Losses |  | 3422.0829 | 43695727.9528 | 69976979.6195 | 96912359.1003 | 125425647.6209 | 154276549.5819 | 183857721.906 | 218006935.9381 | 253242882.4631 | 291694873.82 | 335399908.0463 | 383237420.3631 | 435433512.6966 | 490021278.2894 | 542217767.722 | 600460367.8361 | 664686122.2265 | 732596557.4628 | 804752651.6749 | 881655915.0639 | 967113779.2975 | 1049031666.0505 | 1138505963.9828 | 1227725832.6188 | 1321556451.3743 | 1425756980.6864 | 1537477847.9374 | 1635021600.1266 | 1751390391.1494
Project Cost |  | 923
Benefit-Cost Ratio |  | 3.7076
Market Participation Revenue (All costs are $x1,000) |  |  | 5594.0223 | 6540.7404 | 7487.4584 | 8434.1764 | 9380.8944 | 10327.6124 | 11380.9479 | 12434.2834 | 13487.6189 | 14540.9543 | 15594.2898 | 16380.2946 | 17166.2994 | 17952.3043 | 18738.3091 | 19524.3139 | 20191.7603 | 20859.2068 | 21526.6532 | 22194.0996 | 22861.5461 | 23366.5391 | 23871.5322 | 24376.5253 | 24881.5184 | 25386.5114 | 25670.3387 | 25954.166

## MiraLoma & Centralized BESS VS
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Mira Loma and Centralized BESS in Valley South | Losses (MWh) | 48849.325 | 49618.5 | 50168.1635 | 50717.8269 | 51267.4904 | 51817.1538 | 52366.8173 | 52916.4808 | 53466.1442 | 54015.8077 | 54565.4712 | 55115.1346 | 55664.7981 | 56214.4615 | 56764.125 | 57313.7885 | 57863.4519 | 58413.1154 | 58962.7788 | 59512.4423 | 60062.1058 | 60611.7692 | 61161.4327 | 61711.0962 | 62260.7596 | 62810.4231 | 63360.0865 | 63909.75
N-1 |  | EENS | 1.3 | 10.6 | 21.7833 | 32.9667 | 44.15 | 55.3333 | 66.5167 | 77.7 | 100.68 | 123.66 | 146.64 | 169.62 | 192.6 | 209.84 | 227.08 | 244.32 | 261.56 | 278.8 | 312.4 | 346 | 379.6 | 413.2 | 446.8 | 483.34 | 519.88 | 556.42 | 592.96 | 629.5
N-1 |  | IP | 1.2 | 4.4 | 5.6667 | 6.9333 | 8.2 | 9.4667 | 10.7333 | 12 | 14.58 | 17.16 | 19.74 | 22.32 | 24.9 | 24.6 | 24.3 | 24 | 23.7 | 23.4 | 25.92 | 28.44 | 30.96 | 33.48 | 36 | 36.42 | 36.84 | 37.26 | 37.68 | 38.1
N-1 |  | SAIDI | 0.0026789 | 0.043686 | 0.20986 | 0.37604 | 0.54221 | 0.70839 | 0.87456 | 1.0407 | 2.1026 | 3.1645 | 4.2264 | 5.2883 | 6.3501 | 8.0655 | 9.7809 | 11.4963 | 13.2116 | 14.927 | 18.3573 | 21.7876 | 25.2179 | 28.6482 | 32.0785 | 35.2329 | 38.3873 | 41.5417 | 44.6962 | 47.8506
N-1 |  | SAIFI | 0.0013394 | 0.010921 | 0.022444 | 0.033967 | 0.045489 | 0.057012 | 0.068534 | 0.080057 | 0.10373 | 0.12741 | 0.15109 | 0.17476 | 0.19844 | 0.21649 | 0.23453 | 0.25257 | 0.27062 | 0.28866 | 0.32375 | 0.35883 | 0.39392 | 0.42901 | 0.4641 | 0.50274 | 0.54138 | 0.58003 | 0.61867 | 0.65731
N-1 |  | PFD | 2 | 4 | 5.5 | 7 | 8.5 | 10 | 11.5 | 13 | 16.8 | 20.6 | 24.4 | 28.2 | 32 | 36.4 | 40.8 | 45.2 | 49.6 | 54 | 58.2 | 62.4 | 66.6 | 70.8 | 75 | 78.8 | 82.6 | 86.4 | 90.2 | 94
N-1 |  | Deficit Flex-1 | 1062.8605 | 2091.4079 | 3119.9552 | 4148.5026 | 5177.05 | 6205.5974 | 7234.1448 | 8262.6922 | 9291.2396 | 10319.787 | 11348.3344 | 12376.8818 | 13405.4291 | 14433.9765 | 15462.5239 | 16491.0713 | 17519.6187 | 18548.1661 | 19576.7135 | 20605.2609 | 21633.8083 | 22662.3557 | 23690.903 | 24719.4504 | 25747.9978 | 26776.5452 | 27805.0926 | 28833.64
N-1 |  | Deficit Flex-2-1 | 141086.1703 | 144165.8249 | 147245.4795 | 149074.5129 | 150919.1791 | 152748.2126 | 154733.5737 | 156703.302 | 158673.0303 | 160642.7586 | 162659.3853 | 164676.0119 | 166708.2713 | 168724.8979 | 170678.9934 | 172633.089 | 174602.8173 | 176556.9129 | 178370.3136 | 180183.7142 | 181997.1149 | 183794.8828 | 185405.0576 | 186999.5995 | 188594.1415 | 190204.3163 | 191564.3668 | 192924.4173
N-1 |  | Deficit Flex-2-2 | 19646.6116 | 22588.9977 | 25771.7274 | 27776.2169 | 29895.4423 | 32061.7027 | 34501.4657 | 37006.1427 | 39617.2378 | 42313.5335 | 45181.1572 | 48158.5713 | 51239.6044 | 54402.5593 | 57566.8434 | 60844.4676 | 64280.1918 | 67798.262 | 71155.8742 | 74572.3372 | 78072.1136 | 81601.9699 | 84794.9115 | 87999.2796 | 91257.1915 | 94604.8895 | 97466.769 | 100353.2241
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 277.6027 | 3055.4869 | 5833.3711 | 8611.2553 | 11389.1395 | 14167.0237 | 16944.9079 | 19722.7921 | 26840.726 | 33958.6599 | 41076.5938 | 48194.5278 | 55312.4617 | 62347.7166 | 69382.9715 | 76418.2264 | 83453.4813 | 90488.7362 | 107611.4285 | 124734.1208 | 141856.8131 | 158979.5054 | 176102.1977 | 203735.5548 | 231368.9118 | 259002.2688 | 286635.6259 | 314268.9829
N-1 Monetized | Commercial | $ | 1151.9084 | 3929.7926 | 6707.6768 | 9485.561 | 12263.4452 | 15041.3294 | 17819.2136 | 81839.4462 | 88957.3802 | 96075.3141 | 103193.248 | 110311.1819 | 229518.276 | 258710.9665 | 265746.2214 | 272781.4763 | 279816.7312 | 375481.7285 | 446532.0976 | 517582.4667 | 588632.8358 | 659683.2049 | 730733.574 | 845397.7974 | 960062.0208 | 1074726.2442 | 1189390.4676 | 1304054.691
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5799348.3161 | 6749515.6315 | 7911536.0081 | 8597773.9763 | 9445306.7755 | 10346308.0212 | 11371463.4842 | 12358291.3553 | 13547148.5583 | 14761620.3982 | 16103849.337 | 17426439.1394 | 18990300.6754 | 20402738.5742 | 22102205.4319 | 23864301.0625 | 25807425.4381 | 27807521.7728 | 29903301.334 | 32003476.8101 | 34220806.1238 | 36624387.6081 | 39001620.985 | 41268160.1828 | 43492662.3518 | 46176949.5455 | 48732660.6199 | 51272555.4284
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 14837.8327 | Losses (MWh) | 1232.425 | 1269.55 | 1316.3904 | 1363.2308 | 1410.0712 | 1456.9115 | 1503.7519 | 1550.5923 | 1597.4327 | 1644.2731 | 1691.1135 | 1737.9538 | 1784.7942 | 1831.6346 | 1878.475 | 1925.3154 | 1972.1558 | 2018.9962 | 2065.8365 | 2112.6769 | 2159.5173 | 2206.3577 | 2253.1981 | 2300.0385 | 2346.8788 | 2393.7192 | 2440.5596 | 2487.4
| 759493.06 | Losses ($) | 49297 | 52051.55 | 55321.3059 | 58722.0174 | 62258.1887 | 65934.4672 | 69755.6483 | 73726.6794 | 77852.6648 | 82138.8703 | 86590.7282 | 91213.8421 | 96013.9926 | 100997.1419 | 106169.4399 | 111537.2297 | 117107.053 | 122885.6567 | 128879.9987 | 135097.2542 | 141544.8225 | 148230.3335 | 155161.6545 | 162346.8976 | 169794.4268 | 177512.8656 | 185511.1049 | 193798.3106
N-1 | 8472.3643 | EENS | 16.7 | 29.4 | 50.05 | 70.7 | 91.35 | 112 | 132.65 | 153.3 | 247.42 | 341.54 | 435.66 | 529.78 | 796.05 | 1068.06 | 1340.07 | 1612.08 | 1884.09 | 2156.1 | 2802.57 | 3449.04 | 4095.51 | 4741.98 | 4815.9 | 5573.94 | 6331.98 | 7090.02 | 7848.06 | 8606.1
N-1 | 133.6977 | IP | 2.3 | 1.6 | 3.2167 | 4.8333 | 6.45 | 8.0667 | 9.6833 | 11.3 | 11.67 | 12.04 | 12.41 | 12.78 | 14.6 | 19.3 | 24 | 28.7 | 33.4 | 38.1 | 37.56 | 37.02 | 36.48 | 35.94 | 35.4 | 46.38 | 57.36 | 68.34 | 79.32 | 90.3
N-1 | 1082.0563 | SAIDI | 0.20072 | 0.41236 | 0.92253 | 1.4327 | 1.9429 | 2.4531 | 2.9632 | 3.4734 | 7.6508 | 11.8282 | 16.0057 | 20.1831 | 47.7866 | 74.7367 | 101.6868 | 128.6369 | 155.5869 | 182.537 | 287.2418 | 391.9466 | 496.6515 | 601.3563 | 706.0611 | 942.124 | 1178.1868 | 1414.2497 | 1650.3126 | 1886.3755
N-1 | 7.2857 | SAIFI | 0.012666 | 0.020002 | 0.035147 | 0.050292 | 0.065437 | 0.080582 | 0.095728 | 0.11087 | 0.19214 | 0.27341 | 0.35468 | 0.43594 | 0.67396 | 0.9176 | 1.1612 | 1.4049 | 1.6485 | 1.8922 | 2.3769 | 2.8617 | 3.3464 | 3.8311 | 4.3159 | 5.0108 | 5.7058 | 6.4007 | 7.0957 | 7.7907
N-1 | 494.9928 | PFD | 16 | 24 | 27.8333 | 31.6667 | 35.5 | 39.3333 | 43.1667 | 47 | 50.2 | 53.4 | 56.6 | 59.8 | 65.8333 | 71.2667 | 76.7 | 82.1333 | 87.5667 | 93 | 100.2 | 107.4 | 114.6 | 121.8 | 129 | 136.6 | 144.2 | 151.8 | 159.4 | 167
N-1 | 213597.0269 | Flex-1 | 5264.1735 | 7499.1593 | 9734.1451 | 11969.1308 | 14204.1166 | 16439.1024 | 18674.0882 | 20909.074 | 23144.0598 | 25379.0455 | 27614.0313 | 29849.0171 | 32084.0029 | 34318.9887 | 36553.9744 | 38788.9602 | 41023.946 | 43258.9318 | 45493.9176 | 47728.9034 | 49963.8891 | 52198.8749 | 54433.8607 | 56668.8465 | 58903.8323 | 61138.818 | 63373.8038 | 65608.7896
N-1 | 512526.5558 | Flex-2-1 | 53526.3656 | 53803.8624 | 54081.3592 | 54246.167 | 54412.3834 | 54577.1912 | 54756.0851 | 54933.5704 | 55111.0557 | 55288.541 | 55470.2521 | 55651.9632 | 55835.083 | 56016.7941 | 56192.8708 | 56368.9475 | 56546.4328 | 56722.5095 | 56885.9086 | 57049.3078 | 57212.7069 | 57374.6975 | 57519.7847 | 57663.4632 | 57807.1418 | 57952.229 | 58074.7784 | 58197.3277
N-1 | 587736.118 | Flex-2-2 | 41367.3533 | 44921.2822 | 48605.8473 | 50842.0091 | 53093.5392 | 55327.7006 | 57819.85 | 60354.3856 | 62941.1165 | 65589.4656 | 68329.125 | 71056.9733 | 73863.7141 | 76659.0939 | 79360.5347 | 82084.0016 | 84816.038 | 87557.6214 | 90131.8465 | 92758.2141 | 95413.3179 | 98135.5955 | 100603.0202 | 103061.6099 | 105548.0436 | 108081.7414 | 110260.07 | 112469.5042
N-0 | 21183.8076 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 | 1335.7024 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 | 1756.8124 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 | 22.5453 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 | 284.3733 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 4251371.195 | 2386.5697 | 3641.1696 | 9462.7709 | 15284.3721 | 21105.9734 | 26927.5746 | 32749.1759 | 38570.7772 | 79014.1974 | 119457.6177 | 159901.0379 | 200344.4582 | 337225.1938 | 474188.6084 | 611152.023 | 748115.4376 | 885078.8523 | 1022042.2669 | 1349341.0682 | 1676639.8695 | 2003938.6708 | 2331237.4722 | 2658536.2735 | 3184804.7153 | 3711073.1571 | 4237341.5988 | 4763610.0406 | 5289878.4824
Commerical(N-1) | EENS | 17859705.0151 | 9903.037 | 23857.8886 | 56763.4474 | 89669.0063 | 122574.5651 | 155480.124 | 188385.6828 | 160048.8932 | 350286.1245 | 540523.3558 | 730760.587 | 920997.8183 | 1399311.1628 | 1967638.9109 | 2558124.0945 | 3148609.2781 | 3739094.4618 | 4240949.903 | 5599071.6409 | 6957193.3788 | 8315315.1167 | 9673436.8547 | 11031558.5926 | 13215302.034 | 15399045.4754 | 17582788.9168 | 19766532.3582 | 21950275.7996
Aggregate | EENS | 22111076.2101 | 12289.6066 | 27499.0582 | 66226.2183 | 104953.3784 | 143680.5385 | 182407.6986 | 221134.8587 | 198619.6704 | 429300.3219 | 659980.9734 | 890661.625 | 1121342.2765 | 1736536.3566 | 2441827.5193 | 3169276.1175 | 3896724.7158 | 4624173.3141 | 5262992.1699 | 6948412.7091 | 8633833.2484 | 10319253.7876 | 12004674.3268 | 13690094.8661 | 16400106.7493 | 19110118.6324 | 21820130.5156 | 24530142.3988 | 27240154.282
Residential (N-0) | EENS | 122402385.4505 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17866466.9567 | 20996797.7861 | 24698098.9882 | 28840317.3417 | 33541217.3533 | 38471074.1279 | 44538095.4972 | 50065147.4545 | 56027611.2185 | 61953016.927 | 68192076.4928 | 75753576.0548 | 84072896.7752 | 90296154.7352 | 99941321.9255
Commerical(N-0) | EENS | 524690134.185 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 77675195.1106 | 90392543.5661 | 106694968.7558 | 124345366.1109 | 143712431.512 | 164558346.4294 | 190732503.3698 | 211736495.7562 | 237640870.2909 | 261024283.4324 | 285410828.6852 | 316389312.3519 | 351526819.4674 | 372036180.3666 | 405152985.562
Aggregate | EENS | 647092519.6355 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 95541662.0673 | 111389341.3522 | 131393067.744 | 153185683.4525 | 177253648.8653 | 203029420.5574 | 235270598.867 | 261801643.2106 | 293668481.5094 | 322977300.3594 | 353602905.1779 | 392142888.4066 | 435599716.2426 | 462332335.1019 | 505094307.4875
Residential (N-1) | Value for Flex-1 | 1148319648.5867 | 23076.7301 | 30326551.5538 | 40348940.0606 | 50853493.898 | 61858057.3398 | 73381065.5199 | 85441562.8233 | 98059221.8258 | 111254362.8017 | 125047973.8128 | 139461731.3976 | 154518021.8781 | 170239963.3005 | 186651428.0303 | 203777066.0195 | 221642328.7657 | 240273493.9829 | 259697691.0055 | 279942926.9455 | 301038113.6257 | 323013095.3105 | 345898677.2585 | 369726655.1193 | 394529845.1999 | 420342115.6251 | 447198418.4183 | 475134822.5289 | 504188547.8335
Commerical(N-1) | Value for Flex-1 | 4808351157.0716 | 85560882.9596 | 124934247.8331 | 166222805.3985 | 209497706.9372 | 254832464.2995 | 302303023.4631 | 351987840.2947 | 403967958.5781 | 458327090.3756 | 515151698.7888 | 574531083.1913 | 636557467.002 | 701326088.0764 | 768935291.7875 | 839486626.8792 | 913084944.1681 | 989838498.1797 | 1069859051.8017 | 1153261984.0434 | 1240166400.9899 | 1330695250.0437 | 1424975437.5495 | 1523137949.8994 | 1625317978.2182 | 1731655046.7344 | 1842293144.9399 | 1957380863.6515 | 2077071535.0831
Aggregate | Value for Flex-1 | 5956670805.6583 | 85583959.6897 | 155260799.3869 | 206571745.4591 | 260351200.8352 | 316690521.6393 | 375684088.983 | 437429403.1179 | 502027180.4039 | 569581453.1773 | 640199672.6016 | 713992814.5889 | 791075488.8801 | 871566051.3768 | 955586719.8178 | 1043263692.8987 | 1134727272.9338 | 1230111992.1626 | 1329556742.8072 | 1433204910.989 | 1541204514.6156 | 1653708345.3541 | 1770874114.808 | 1892864605.0187 | 2019847823.4182 | 2151997162.3595 | 2289491563.3582 | 2432515686.1804 | 2581260082.9166
Residential (N-1) | Value for Flex-2 | 21148393.0448 | 1782193.5022 | 1836218.755 | 1891831.3995 | 1945036.4893 | 1999771.2084 | 2055973.9519 | 2114280.8795 | 2174162.4195 | 2235716.611 | 2298989.6605 | 2364209.1501 | 2431252.7456 | 2500233.9663 | 2571080.0621 | 2643640.7387 | 2718222.5242 | 2794950.7478 | 2873745.1286 | 2954074.043 | 3036623.3124 | 3121453.7491 | 3208549.0445 | 3297079.2821 | 3387947.9271 | 3481299.3297 | 3577287.7863 | 3674473.8539 | 3774283.4201
Commerical(N-1) | Value for Flex-2 | 95329595.2411 | 8033508.0235 | 8277035.0599 | 8527717.5055 | 8767547.5323 | 9014272.596 | 9267615.0027 | 9530442.3385 | 9800367.4794 | 10077832.351 | 10363045.2364 | 10657031.996 | 10959241.1904 | 11270184.5248 | 11589534.0667 | 11916612.3427 | 12252801.0738 | 12598665.2007 | 12953842.8453 | 13315937.6334 | 13688041.0091 | 14070427.0927 | 14463022.3713 | 14862085.8699 | 15271690.0949 | 15692485.7275 | 16125168.2812 | 16563249.2489 | 17013156.0349
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 116477988.2859 | 9815701.5258 | 10113253.8149 | 10419548.9051 | 10712584.0215 | 11014043.8044 | 11323588.9546 | 11644723.2179 | 11974529.8989 | 12313548.962 | 12662034.897 | 13021241.1461 | 13390493.936 | 13770418.4911 | 14160614.1287 | 14560253.0814 | 14971023.598 | 15393615.9485 | 15827587.9738 | 16270011.6764 | 16724664.3216 | 17191880.8418 | 17671571.4158 | 18159165.152 | 18659638.022 | 19173785.0573 | 19702456.0675 | 20237723.1028 | 20787439.455
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 188669783.2371 | 10726430.6318 | 11942838.0359 | 13061902.919 | 14045858.0161 | 15047134.0893 | 15966281.3827 | 16826769.1539 | 18031643.2416 | 19121727.879 | 20269467.1635 | 21725569.9002 | 23033944.1605 | 24337982.4887 | 25992222.3359 | 27346151.7604 | 28972813.1979 | 30514933.4016 | 32194753.8374 | 33748293.6103 | 35525086.7882 | 37174742.0752 | 38757026.5048 | 40665669.1094 | 42764617.4428 | 44906575.7851 | 46928961.0327 | 48645205.3735 | 50869866.9434
Aggregate ($M) |  | 6931.0222 | 108076921.4964 | 182438236.1407 | 237860566.0342 | 296016357.9777 | 355877640.0604 | 417788078.1672 | 485650721.3711 | 556379677.5959 | 631801083.7439 | 714136528.4339 | 802576890.3309 | 896962092.3677 | 995395396.7406 | 1093723045.869 | 1199728715.2103 | 1313960902.1895 | 1433830398.2793 | 1560095725.6536 | 1693201049.5422 | 1837358697.8408 | 1980195865.2693 | 2132975868.5648 | 2288356834.5056 | 2451275090.8101 | 2627330530.2409 | 2813542827.2165 | 2988261092.1574 | 3185251851.0846
Aggregate ($M)+ Monetized Losses |  | 6931.7817 | 108126218.4964 | 182490287.6907 | 237915887.3401 | 296075079.9951 | 355939898.249 | 417854012.6344 | 485720477.0194 | 556453404.2753 | 631878936.4087 | 714218667.3043 | 802663481.0591 | 897053306.2098 | 995491410.7332 | 1093824043.0109 | 1199834884.6502 | 1314072439.4191 | 1433947505.3323 | 1560218611.3103 | 1693329929.5408 | 1837493795.095 | 1980337410.0919 | 2133124098.8983 | 2288511996.1601 | 2451437437.7077 | 2627500324.6677 | 2813720340.0822 | 2988446603.2624 | 3185445649.3952
Project Cost |  | 829
Benefit-Cost Ratio |  | 8.3616
Market Participation Revenue (All costs are $x1,000) | [7 empty] | 4759.5264 | 5629.0106 | 6498.4947 | 7367.9789 | 8237.4631 | 9106.9472 | 10185.1716 | 11263.3959 | 12341.6202 | 13419.8445 | 14498.0689 | 15431.8013 | 16365.5338 | 17299.2663 | 18232.9987 | 19166.7312 | 19576.9446 | 19987.158 | 20397.3714 | 20807.5847 | 21217.7981 | 21455.8675 | 21693.9369

## VS to VN & Distributed BESS VS
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Valley South to Valley North and Distributed BESS in Valley South | Losses (MWh) | 49722.95 | 50479.4 | 51032.9519 | 51586.5038 | 52140.0558 | 52693.6077 | 53247.1596 | 53800.7115 | 54354.2635 | 54907.8154 | 55461.3673 | 56014.9192 | 56568.4712 | 57122.0231 | 57675.575 | 58220.3323 | 58765.0896 | 59309.8468 | 59854.6041 | 60399.3614 | 60944.1187 | 61488.876 | 62033.6332 | 62578.3905 | 63123.1478 | 63667.9051 | 64212.6624 | 64748.625
N-1 |  | EENS | 12.4 | 31.9 | 62.6333 | 93.3667 | 124.1 | 154.8333 | 185.5667 | 216.3 | 328.58 | 440.86 | 553.14 | 665.42 | 777.7 | 985.26 | 1192.82 | 1400.38 | 1607.94 | 1815.5 | 2189.64 | 2563.78 | 2937.92 | 3312.06 | 3686.2 | 4151.36 | 4616.52 | 5081.68 | 5546.84 | 6012
N-1 |  | IP | 5.9 | 10.3 | 13.3 | 16.3 | 19.3 | 22.3 | 25.3 | 28.3 | 31.04 | 33.78 | 36.52 | 39.26 | 42 | 49.5 | 57 | 64.5 | 72 | 79.5 | 79.04 | 78.58 | 78.12 | 77.66 | 77.2 | 88.76 | 100.32 | 111.88 | 123.44 | 135
N-1 |  | SAIDI | 0.045307 | 0.1457 | 0.86574 | 1.5858 | 2.3058 | 3.0259 | 3.7459 | 4.466 | 9.4602 | 14.4544 | 19.4486 | 24.4428 | 29.437 | 50.8028 | 72.1685 | 93.5342 | 114.8999 | 136.2656 | 195.2029 | 254.1402 | 313.0774 | 372.0147 | 430.952 | 534.632 | 638.3121 | 741.9921 | 845.6722 | 949.3523
N-1 |  | SAIFI | 0.011327 | 0.029139 | 0.057236 | 0.085333 | 0.11343 | 0.14153 | 0.16962 | 0.19772 | 0.30223 | 0.40674 | 0.51126 | 0.61577 | 0.72028 | 0.91293 | 1.1056 | 1.2982 | 1.4909 | 1.6835 | 2.0345 | 2.3855 | 2.7365 | 3.0875 | 3.4385 | 3.8738 | 4.309 | 4.7443 | 5.1795 | 5.6147
N-1 |  | PFD | 4 | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 27.2 | 31.4 | 35.6 | 39.8 | 44 | 52.2 | 60.4 | 68.6 | 76.8 | 85 | 93.6 | 102.2 | 110.8 | 119.4 | 128 | 137.6 | 147.2 | 156.8 | 166.4 | 176
N-1 |  | Deficit Flex-1 | 4238.9824 | 6425.4824 | 8611.9824 | 10798.4824 | 12984.9824 | 15171.4824 | 17357.9824 | 19544.4824 | 21730.9824 | 23917.4824 | 26103.9824 | 28290.4824 | 30476.9824 | 32663.4824 | 34005.5498 | 35347.6172 | 36689.6845 | 38031.7519 | 39373.8192 | 40715.8866 | 42057.954 | 43400.0213 | 44742.0887 | 46084.156 | 47426.2234 | 48768.2908 | 50110.3581 | 51452.4255
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 17164.3208 | 19844.0887 | 22754.5274 | 24601.2435 | 26524.5104 | 28541.0948 | 30814.4348 | 33148.2171 | 35561.9498 | 38077.7187 | 40736.7643 | 43501.2116 | 46385.9444 | 49358.9359 | 52298.7216 | 54844.3439 | 58041.2882 | 60818.499 | 64000.8853 | 67013.2688 | 70120.491 | 73268.9515 | 76136.8129 | 79027.7015 | 81953.9878 | 84693.4351 | 86996.7698 | 89856.6833
N-0 |  | EENS(Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 16.85 | 32.3 | 47.75 | 63.2 | 92.7 | 125.4727 | 158.2455 | 191.0182 | 223.7909 | 360.5
N-0 |  | EENS(Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.15 | 152.3 | 228.45 | 304.6 | 721.28 | 1137.96 | 1554.64 | 1971.32 | 2388 | 3345.9467 | 4303.8933 | 5261.84 | 6219.7867 | 7719 | 8977.5164 | 10236.0327 | 11494.5491 | 12753.0655 | 15815
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 27.8 | 41.7 | 55.6 | 73.16 | 90.72 | 108.28 | 125.84 | 143.4 | 164.56 | 185.72 | 206.88 | 228.04 | 252.8 | 275.1055 | 297.4109 | 319.7164 | 342.0218 | 371.2
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1631 | 2.3261 | 3.4892 | 4.6523 | 31.7782 | 58.9041 | 86.0301 | 113.156 | 140.2819 | 266.6571 | 393.0322 | 519.4073 | 645.7824 | 871.4067 | 1113.2864 | 1355.1661 | 1597.0458 | 1838.9255 | 2773.8327
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15173 | 0.30347 | 0.4552 | 0.60693 | 1.0469 | 1.4869 | 1.9269 | 2.3668 | 2.8068 | 3.9362 | 5.0657 | 6.1951 | 7.3245 | 9.1434 | 10.1323 | 11.1212 | 12.1102 | 13.0991 | 13.2449
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.25 | 6.5 | 9.75 | 13 | 20.6 | 28.2 | 35.8 | 43.4 | 51 | 60.7667 | 70.5333 | 80.3 | 90.0667 | 102 | 112.5091 | 123.0182 | 133.5273 | 144.0364 | 159
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121943.8344 | 557395.4427 | 1230664.8375 | 2104893.335 | 3208711.836 | 5074358.4432 | 7294231.1079 | 10621351.0983 | 15163062.8948 | 20401738.6155 | 25584139.4626 | 32828440.9099 | 40824564.5109 | 49073877.304 | 59455154.4736 | 70544240.6181 | 82573459.218 | 93886167.6922 | 106217109.6912
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729516.8638 | 3180050.4533 | 6467576.6035 | 9571528.7893 | 13952844.5382 | 22407387.6493 | 31401817.2979 | 46733580.8761 | 67174413.0033 | 89726211.0548 | 108641376.863 | 139289538.0636 | 173823253.624 | 205957531.8258 | 249996426.6328 | 296972112.599 | 347542804.7365 | 390421188.6183 | 440013691.4765
N-1 Monetized | Residential | $ | 2647.9026 | 6982.2415 | 14894.8627 | 22807.4839 | 30720.1051 | 38632.7263 | 46545.3475 | 54457.9686 | 49788.3405 | 45118.7124 | 40449.0844 | 35779.4563 | 257477.5314 | 365660.9705 | 473844.4096 | 582027.8487 | 690211.2877 | 684880.0907 | 881770.233 | 1078660.3752 | 1275550.5175 | 1472440.6597 | 1669330.802 | 1960393.624 | 2251456.446 | 2542519.2679 | 2833582.0899 | 3124644.9119
N-1 Monetized | Commercial | $ | 10987.4343 | 28972.7123 | 61806.0218 | 94639.3312 | 127472.6407 | 160305.9502 | 193139.2597 | 225972.5691 | 206596.0135 | 187219.4579 | 167842.9023 | 148466.3467 | 1068399.368 | 1517305.0153 | 1966210.6627 | 2415116.3101 | 2864021.9575 | 2841900.231 | 3658893.0861 | 4475885.9413 | 5292878.7964 | 6109871.6516 | 6926864.5067 | 8134625.5618 | 9342386.617 | 10550147.6721 | 11757908.7272 | 12965669.7823
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5110374.2214 | 6015097.5811 | 6967510.5921 | 7745187.9968 | 8491036.7137 | 9233048.7464 | 10172667.8173 | 11216525.0586 | 12260160.0595 | 13330830.0069 | 14604368.7155 | 15898045.9904 | 17328004.7347 | 18766389.6983 | 20232001.0865 | 21637239.3753 | 23415873.1683 | 25127984.3404 | 27049783.8804 | 28952045.9033 | 30960752.5471 | 33118259.9874 | 35150034.7536 | 37379953.3141 | 39694609.5816 | 41939674.8036 | 43745512.9395 | 46284092.6758
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 6646.3476 | Losses (MWh) | 358.8 | 408.65 | 451.6019 | 494.5538 | 537.5058 | 580.4577 | 623.4096 | 666.3615 | 709.3135 | 752.2654 | 795.2173 | 838.1692 | 881.1212 | 924.0731 | 967.025 | 1018.7716 | 1070.5181 | 1122.2647 | 1174.0113 | 1225.7578 | 1277.5044 | 1329.251 | 1380.9975 | 1432.7441 | 1484.4907 | 1536.2372 | 1587.9838 | 1648.525
| 354648.5554 | Losses ($) | 14352 | 16754.65 | 18978.5708 | 21303.216 | 23732.2319 | 26269.384 | 28918.5611 | 31683.7787 | 34569.1831 | 37579.0553 | 40717.8154 | 43990.0266 | 47400.3997 | 50953.7977 | 54655.2404 | 59019.3996 | 63567.6074 | 68306.3383 | 73242.2761 | 78382.3193 | 83733.5882 | 89303.4316 | 95099.4337 | 101129.4213 | 107401.4711 | 113923.9175 | 120705.3603 | 128439.881
N-1 | 2641.0479 | EENS | 5.6 | 8.1 | 9.2 | 10.3 | 11.4 | 12.5 | 13.6 | 14.7 | 19.52 | 24.34 | 29.16 | 33.98 | 210.95 | 292.64 | 374.33 | 456.02 | 537.71 | 619.4 | 925.33 | 1231.26 | 1537.19 | 1843.12 | 1576.5 | 1905.92 | 2235.34 | 2564.76 | 2894.18 | 3223.6
N-1 | -52.4992 | IP | -2.4 | -4.3 | -4.4167 | -4.5333 | -4.65 | -4.7667 | -4.8833 | -5 | -4.79 | -4.58 | -4.37 | -4.16 | -2.5 | -5.6 | -8.7 | -11.8 | -14.9 | -18 | -15.56 | -13.12 | -10.68 | -8.24 | -5.8 | -5.96 | -6.12 | -6.28 | -6.44 | -6.6
N-1 | 486.0227 | SAIDI | 0.15809 | 0.31035 | 0.26665 | 0.22296 | 0.17926 | 0.13557 | 0.091871 | 0.048175 | 0.29325 | 0.53833 | 0.78341 | 1.0285 | 24.6997 | 31.9995 | 39.2992 | 46.5989 | 53.8987 | 61.1984 | 110.3962 | 159.5941 | 208.7919 | 257.9898 | 307.1876 | 442.7248 | 578.2621 | 713.7993 | 849.3366 | 984.8738
N-1 | 1.9948 | SAIFI | 0.0026789 | 0.0017839 | 0.00035493 | -0.001074 | -0.0025029 | -0.0039318 | -0.0053607 | -0.0067897 | -0.0063576 | -0.0059256 | -0.0054935 | -0.0050615 | 0.15211 | 0.22116 | 0.2902 | 0.35925 | 0.42829 | 0.49733 | 0.66616 | 0.83498 | 1.0038 | 1.1726 | 1.3415 | 1.6398 | 1.9382 | 2.2365 | 2.5349 | 2.8332
N-1 | 367.8665 | PFD | 14 | 23 | 25.3333 | 27.6667 | 30 | 32.3333 | 34.6667 | 37 | 39.8 | 42.6 | 45.4 | 48.2 | 53.8333 | 55.4667 | 57.1 | 58.7333 | 60.3667 | 62 | 64.8 | 67.6 | 70.4 | 73.2 | 76 | 77.8 | 79.6 | 81.4 | 83.2 | 85
N-1 | 108576.8331 | Flex-1 | 2088.0515 | 3165.0847 | 4242.1179 | 5319.151 | 6396.1842 | 7473.2174 | 8550.2506 | 9627.2837 | 10704.3169 | 11781.3501 | 12858.3832 | 13935.4164 | 15012.4496 | 16089.4828 | 18010.9486 | 19932.4144 | 21853.8802 | 23775.346 | 25696.8118 | 27618.2776 | 29539.7434 | 31461.2093 | 33382.6751 | 35304.1409 | 37225.6067 | 39147.0725 | 41068.5383 | 42990.0041
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 628140.4285 | Flex-2-2 | 43849.6441 | 47666.1912 | 51623.0473 | 54016.9826 | 56464.4711 | 58848.3085 | 61506.8809 | 64212.3112 | 66996.4044 | 69825.2804 | 72773.518 | 75714.333 | 78717.3741 | 81702.7173 | 84628.6566 | 88084.1253 | 91054.9416 | 94537.3844 | 97286.8354 | 100317.2825 | 103364.9405 | 106468.614 | 109261.1187 | 112033.1881 | 114851.2474 | 117993.1958 | 120730.0692 | 122966.045
N-0 | 10787.9436 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1509.75 | 1772.8 | 2035.85 | 2539.0833 | 2701.7867 | 2864.49 | 3027.1933 | 3189.8967 | 3351.2 | 3207.2033 | 3063.2067 | 2919.21 | 2775.2133 | 2075.9 | 1711.5709 | 1347.2418 | 982.9127 | 618.5836 | -1653.1
N-0 | 903.2213 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 146.8 | 147.55 | 148.3 | 149.4 | 146.84 | 144.28 | 141.72 | 139.16 | 136.6 | 129.12 | 121.64 | 114.16 | 106.68 | 95.6 | 85.7345 | 75.8691 | 66.0036 | 56.1382 | 39.4
N-0 | 610.7 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 52.594 | 69.1341 | 85.6743 | 139.9104 | 168.1836 | 196.4568 | 224.73 | 253.0032 | 281.2764 | 285.2601 | 289.2438 | 293.2275 | 297.2112 | 201.9457 | 184.3384 | 166.7311 | 149.1238 | 131.5165 | -579.1183
N-0 | 10.892 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.5361 | 1.7454 | 1.9546 | 2.4195 | 2.5962 | 2.7728 | 2.9495 | 3.1261 | 3.3027 | 3.056 | 2.8093 | 2.5626 | 2.3158 | 1.3796 | 1.3773 | 1.3749 | 1.3725 | 1.3701 | 2.2108
N-0 | 126.5246 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 24.75 | 26 | 27.25 | 29.3333 | 27.0667 | 24.8 | 22.5333 | 20.2667 | 18 | 14.8333 | 11.6667 | 8.5 | 5.3333 | 0 | -2.5091 | -5.0182 | -7.5273 | -10.0364 | -17
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 1894923.657 | 16.2698 | -285.585 | 401.2792 | 1088.1435 | 1775.0078 | 2461.8721 | 3148.7363 | 3835.6006 | 56066.5829 | 108297.5652 | 160528.5474 | 212759.5297 | 135060.1241 | 170875.3545 | 206690.5849 | 242505.8154 | 278321.0458 | 427650.9123 | 575182.2637 | 722713.6151 | 870244.9665 | 1017776.3179 | 1165307.6692 | 1428146.6461 | 1690985.6229 | 1953824.5997 | 2216663.5766 | 2479502.5534
Commerical(N-1) | EENS | 7862958.8618 | 67.5111 | -1185.0311 | 1665.1025 | 4515.2361 | 7365.3696 | 10215.5032 | 13065.6368 | 15915.7703 | 232647.4911 | 449379.2119 | 666110.9327 | 882842.6535 | 560430.0708 | 709044.862 | 857659.6532 | 1006274.4443 | 1154889.2355 | 1774531.4005 | 2386710.6524 | 2998889.9042 | 3611069.1561 | 4223248.408 | 4835427.6598 | 5926074.2695 | 7016720.8792 | 8107367.4889 | 9198014.0986 | 10288660.7083
Aggregate | EENS | 9757882.5188 | 83.7809 | -1470.6161 | 2066.3817 | 5603.3796 | 9140.3774 | 12677.3752 | 16214.3731 | 19751.3709 | 288714.074 | 557676.7771 | 826639.4801 | 1095602.1832 | 695490.1949 | 879920.2165 | 1064350.2381 | 1248780.2597 | 1433210.2813 | 2202182.3128 | 2961892.9161 | 3721603.5193 | 4481314.1226 | 5241024.7258 | 6000735.3291 | 7354220.9156 | 8707706.5021 | 10061192.0886 | 11414677.6751 | 12768163.2617
Residential (N-0) | EENS | 56609516.0397 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7427041.24 | 9237296.1549 | 11243683.5382 | 13242127.649 | 14657755.1207 | 15922439.3429 | 17403867.8803 | 18218966.2434 | 18378154.4586 | 18069335.5124 | 18953956.0346 | 17236706.5445 | 15203046.7076 | 12879139.623 | 8736922.0192 | 5209335.4366 | 1499437.5572 | -3590012.957 | -6275787.7657
Commerical(N-0) | EENS | 245020687.6768 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32066870.8602 | 39971861.0198 | 49398898.1353 | 59065858.254 | 63722350.5725 | 67985155.9168 | 75293151.4579 | 77611785.2348 | 76538018.5086 | 74832135.3746 | 82091126.5068 | 72446957.6926 | 63817616.6669 | 55066751.6066 | 35414402.0523 | 19417199.7529 | 3984014.7309 | -18385008.2516 | -34860705.9145
Aggregate | EENS | 301630203.7165 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 39493912.1002 | 49209157.1747 | 60642581.6735 | 72307985.903 | 78380105.6932 | 83907595.2598 | 92697019.3382 | 95830751.4782 | 94916172.9672 | 92901470.887 | 101045082.5415 | 89683664.2372 | 79020663.3745 | 67945891.2296 | 44151324.0715 | 24626535.1895 | 5483452.288 | -21975021.2086 | -41136493.6802
Residential (N-1) | Value for Flex-1 | 608241849.8083 | 8238114.0347 | 12799582.0479 | 17583974.6405 | 22599587.1239 | 27854990.2474 | 33359038.7851 | 39120880.3807 | 45149964.6569 | 51456052.5967 | 58049226.2056 | 64939898.462 | 72138823.5649 | 79657107.4864 | 87506218.8392 | 100405450.0461 | 113894951.4265 | 127996174.4697 | 142731274.3204 | 158123131.5546 | 174195374.6041 | 190972402.8488 | 208479410.3966 | 226742410.57 | 245788261.1206 | 265644690.1922 | 286340323.0541 | 307904709.6277 | 330368352.8281
Commerical(N-1) | Value for Flex-1 | 2505732901.1377 | 33938002.4352 | 52729574.3762 | 72439513.6626 | 93101993.9295 | 114752323.5136 | 137426980.8307 | 161163650.8115 | 186001262.4283 | 211980027.3442 | 239141479.7169 | 267528517.1911 | 297185443.1142 | 328158010.0103 | 360493464.3491 | 413633556.6408 | 469205345.1318 | 527297202.0744 | 588000398.5235 | 651409194.0438 | 717620929.0909 | 786736120.1442 | 858858557.6694 | 934095406.9958 | 1012557312.19 | 1094358503.0145 | 1179616905.0602 | 1268454253.1437 | 1360996208.0657
Aggregate | Value for Flex-1 | 3113974750.9461 | 42176116.4699 | 65529156.424 | 90023488.3031 | 115701581.0534 | 142607313.761 | 170786019.6158 | 200284531.1923 | 231151227.0853 | 263436079.941 | 297190705.9225 | 332468415.6531 | 369324266.6791 | 407815117.4966 | 447999683.1883 | 514039006.6868 | 583100296.5583 | 655293376.5441 | 730731672.8439 | 809532325.5984 | 891816303.695 | 977708522.993 | 1067337968.066 | 1160837817.5659 | 1258345573.3106 | 1360003193.2067 | 1465957228.1142 | 1576358962.7714 | 1691364560.8938
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 202521982.9576 | 11415404.7265 | 12677256.0862 | 14005928.335 | 14898443.9956 | 16001404.1511 | 17079540.6575 | 18025564.8207 | 19173409.5383 | 20408716.3778 | 21700257.5548 | 23225050.5217 | 24562337.3095 | 26000278.4294 | 27628571.2119 | 29216356.1057 | 31199874.885 | 32906485.6713 | 34874291.2698 | 36601811.0639 | 38576517.6951 | 40434795.652 | 42263154.1255 | 44517255.3408 | 46652824.3115 | 48704628.5553 | 51166235.7746 | 53632353.054 | 55858329.696
Aggregate ($M) |  | 3627.8848 | 55530145.0197 | 83298787.7388 | 111772625.5526 | 141407390.155 | 171600118.2783 | 202509948.7969 | 237855001.4087 | 274492092.3756 | 314488563.7964 | 358942552.3546 | 405729262.8297 | 455624787.8454 | 506818872.0239 | 554888280.3098 | 628227308.2904 | 708245971.0412 | 785463823.9749 | 862724319.3937 | 941997500.4654 | 1035159507.4509 | 1112308297.0047 | 1193862810.2918 | 1279301699.4653 | 1356503942.6092 | 1442042063.4536 | 1532668108.2654 | 1619430972.2919 | 1718854560.1713
Aggregate ($M)+ Monetized Losses |  | 3628.2395 | 55544497.0197 | 83315542.3888 | 111791604.1234 | 141428693.371 | 171623850.5102 | 202536218.1809 | 237883919.9699 | 274523776.1543 | 314523132.9795 | 358980131.4099 | 405769980.6451 | 455668777.872 | 506866272.4236 | 554939234.1076 | 628281963.5308 | 708304990.4408 | 785527391.5823 | 862792625.732 | 942070742.7415 | 1035237889.7702 | 1112392030.5929 | 1193952113.7234 | 1279396798.8991 | 1356605072.0305 | 1442149464.9247 | 1532782032.1829 | 1619551677.6522 | 1718983000.0523
Project Cost |  | 213
Benefit-Cost Ratio |  | 17.034
Market Participation Revenue (All costs are $x1,000) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2766.0729 | 2798.872 | 2831.6712 | 2864.4703 | 2897.2694 | 2930.0685 | 2964.5016 | 2998.9347 | 3033.902 | 3068.8693 | 3103.8366 | 3139.3439 | 3174.8511

## 7 - Distributed Storage - 30% (hidden)
10% Distributed Storage
| Equipment Categories All costs are $x1,000 | [6 empty] | Units | kV | Cost | Adjusted Cost
1 | New Substation Equipment
| 500kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 36194.3937 | 0 |  | 0
| 115kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 4403.9172 | 1 |  | 4403.9172
| 230kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 17710.3457 | 0 |  | 0
2 | Transformer Banks
| 500/115 kV 1-3 Phase |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 24748.4568 | 0 |  | 0
| 230/115 kV |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 8756.8817 | 1 |  | 8756.8817
kV
3 | Line Positions to terminate ties and Transformer Bank positions |  |  |  | 230 | 500 | 115
| Single Breaker (add third breaker to breaker and a half) |  |  |  | 2145.4637 | 5398.3718 | 1437.1815 | 0 | 115 | 0
| Breaker and a half (2CB) |  |  |  | 3607.9737 | 8587.7771 | 2149.8636 | 0 | 230 | 0
| Breaker and a half (3CB) |  |  |  | 5291.2883 | 12131.4222 | 3436.5983 | 1 | 115 | 3436.5983
| Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | Used in substation expansion |  | 540.3386 |  | 252.4804 | 0 | 115 | 0
4 | Shunt Capacitors | [5 empty] | 2006.8433 | 0 |  | 0
5 | Fiber optic cable on existing poles | /mile |  |  |  | 99 | 99 | 0 |  | 0
| Fiber optic cable on new poles | /mile |  |  |  | 134 | 134 | 0
6 | Single Circuit, Lattice Tower | /mile |  |  | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
[5 empty] | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
| Double Circuit, Strung on both sides, Lattice Tower | /mile |  |  | 4494.8333 | 9381.7495 | 2174.744
| Rebuild/reconductor existing single circuit line section - Metropolitan | /mile |  |  |  |  | 1381.7727 | 0 |  | 0
| Rebuild/reconductor existing double circuit line section - Metropolitan | /mile |  |  |  |  | 1454.8259 | 0 |  | 0
7 | Disconnect switches (incl. steel structures and foundations) |  |  |  | 3326.9104 | 19935.5969 | 105.461 | 0 | 115 | 0 |  | T&D Costs | 16597.3971
8 | Energy Storage |  |  |  |  | Base price
2024 | Battery Price (Power) | $/kW |  |  |  | 175 | #REF! | 337.0822 |  | #REF!
2024 | Battery Price (Energy) | $/kWh |  |  |  | 310 | #REF! | 674.1643 |  | #REF!
2024 | Battery Price (Energy uprate) | $/kWh |  |  |  | 310 | #REF! | 789.8909 |  | #REF!
[12 empty] | ESS-1 | #REF!
2030 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 21.3922 |  | #REF!
2030 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 42.7844 |  | #REF!
2030 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 162.9641 |  | #REF!
[12 empty] | ESS-2 | #REF!
[12 empty] | ESS-2 W escalation | #REF!
2035 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 22.7569 |  | #REF!
2035 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 45.5138 |  | #REF!
2035 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 170.4306 |  | #REF!
2035 | Inverter Replacement | $/kW | [5 empty] | 368.688 |  | #REF! |  | ESS-3 | #REF!
[12 empty] | ESS-3 W escalation | #REF!
2040 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 24.216 |  | #REF!
2040 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 48.4319 |  | #REF!
2040 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 178.3896 |  | #REF!
2040 | Inverter Replacement | MW | [5 empty] | 21.3922 |  | #REF! |  | ESS-4 | #REF!
2040 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF! |  | ESS-4 W escalation | #REF!
2045 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 15.2718 |  | #REF!
2045 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 30.5435 |  | #REF!
2045 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 163.6802 |  | #REF!
2045 | Inverter Replacement | MW | [5 empty] | 22.7569 |  | #REF!
2045 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF!
[12 empty] | ESS-5 | #REF!
[12 empty] | ESS-5 w escalation | #REF!
| Total Cost | [8 empty] | 316263.4365
| Total Cost with Contingency | [8 empty] | #REF!
| Total Cost with SCE Escalation Rate | [8 empty] | #REF!
Factor Amounts: |  |  |  |  | Low Impact factors: |  |  | Medium Impact factors: |  |  | High Impact factors:
| Terrain (CAISO per unit costs) |  |  |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  |  | 2.0X to 3.0X
| Terrain (User specified) |  |  |  |  | 1.25 |  |  | 1.5 |  |  | 2
| Population density (CAISO per unit costs) |  |  |  |  | 1.00X to 1.10X |  |  | 1.33X |  |  | 1.67X
| Population density(User specified) |  |  |  |  | 1.1 |  |  | 1.33 |  |  | 1.67
| Weather study (CAISO per unit costs) |  |  |  |  | 1.35X |  |  | 1.45X |  |  | 1.60X
| Weather study(User specified) |  |  |  |  | 1.35 |  |  | 1.45 |  |  | 1.6
| Factor Type |  |  | Explanation of Factor issues and Factor multipliers
| Terrain |  |  | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
| Population density |  |  | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
| Weather study |  |  | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
[5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2030 and beyond
|  |  |  | Escalation Rate | 2.696% | 2.138% | 2.556% | 2.352% | 2.287% | 2.333% | 2.249% | 2.332% | 2.295% | 2.01% | 2.212% | 0.023
|  |  |  | Escalation Factors | 1 | 1.0214 | 1.0475 | 1.0721 | 1.0966 | 1.1222 | 1.1475 | 1.1742 | 1.2012 | 1.2253 | 1.2524 | 1.2812
| Contingency Factor |  | #REF!
| Contingency Factor for battery | Power | #REF!
|  | Energy | #REF!
Notes
| Contingency Factor included to account for the following considerations |  |  |  | 2018: The SDGE project has been ranked as high impact due to terrain and population, primarily driven by the complications associated with traversing the Pechanga Reservation
o Review of customer/developer existing and proposed plans (i.e. surveyed base map, street/land
improvements, profiles, grading, overhead & underground utilities, temp construction roads &
laydown/staging yards, etc.)
o Property rights study
o Right-of-way improvements/acquisitions (i.e. easements, access/maintenance roads, grading, etc.)
o GO 131-D engineering/permitting per CEQA requirements
o Non-GO 131-D Permitting (i.e. Railroad, City, County, State, Federal Agency, etc.)
o Governing regulation impacts (i.e. CPUC, FERC, OSHA, etc.)
o Environmental study and mitigations
o EMF study and potential reduction mitigations as required by the CPUC
o Geotechnical investigation and mitigations
o Surveys
o Potholing
o Traffic plans/control
o Concrete and/or asphalt repairs
o Associated SCE Substation work (i.e. breaker replacements, switch-rack position relocations, etc.)
o Associated SCE Distribution voltage under-build work (i.e. 16 kV, 12 kV, 4 kV, and secondary
conductors)
o Associated SCE Telecommunication under-build work
o Associated 3rd Party Joint Owners and renters/tenants under-build work (i.e. cable TV,
communication cable, fiber optic, etc.)
o Conflicts associated with other projects in the same geographical area or electrical system
o Availability of line outages required for construction
Unit costs exclude Licensing.
| ESS O&M | #REF! | $/kWh
| + | 1% | of EPC Cost |  | 2020: Add contingency for battery value
| Price Escalation | 2.5% |  |  | 2020: Battery cost reduction = 0%, global factor, and what it changes
| T&D Annual OPEX | #REF! |  |  | 2020: Include 2% into battery price escalation
| Inverter Replacement Cost | #REF! | $/kWh |  | 2020: Make the significant digits, 1000$ of dollars
| Battery Replacement Cost | #REF! | % Capex |  | 2020: shift it to 99 instead of 90, not take actual MW
| Annual Battery Cost Change | #REF!
| Price Stabizes in | #REF!
| Calendar Time (Year) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| O&M T&D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Initial CapEx costs | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| Total Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| MW | 337.0822 | 3.7834 | 3.83 | 3.8771 | 3.9249 | 3.9733 | 4.0224 | 4.0721 | 4.1225 | 4.1736 | 4.2253 | 4.2777 | 4.3309 | 4.3847 | 4.4393 | 4.4946 | 4.5506 | 4.6074 | 4.665 | 4.7233 | 4.7825 | 4.8424 | 4.9031 | 4.9647 | 5.0271 | 5.0903 | 5.1544
| MWh | 674.1643 | 7.5669 | 7.66 | 7.7543 | 7.8498 | 7.9467 | 8.0448 | 8.1443 | 8.245 | 8.3471 | 8.4506 | 8.5555 | 8.6617 | 8.7694 | 8.8786 | 8.9892 | 9.1013 | 9.2149 | 9.33 | 9.4467 | 9.5649 | 9.6848 | 9.8062 | 9.9294 | 10.0541 | 10.1806 | 10.3088
| MWh uprate | 687.6476 | 21.2015 | 21.4478 | 21.6972 | 21.9498 | 22.2055 | 22.4646 | 22.7269 | 22.9925 | 23.2616 | 23.5341 | 23.8101 | 24.0896 | 24.3726 | 24.6593 | 24.9497 | 25.2438 | 25.5417 | 25.8435 | 26.1491 | 26.4586 | 26.7722 | 27.0898 | 27.4115 | 27.7373 | 28.0674 | 28.4018
| Battery price | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902
| Energy price | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804
| Inverter replacement MW | [10 empty] | 337.0822 | 3.7834 | 3.83 | 3.8771 | 3.9249 | 3.9733 | 4.0224 | 4.0721 | 4.1225 | 4.1736 | 4.2253 | 4.2777 | 4.3309 | 4.3847 | 4.4393 | 4.4946 | 4.5506
| Battery costs | 299666.0393 | 8082.6313 | 8176.9725 | 8272.5149 | 8369.2749 | 8467.2694 | 8566.5152 | 8667.0295 | 7149.8643 | 7233.9325 | 7319.0783 | 7405.3166 | 7492.6624 | 7581.1312 | 7670.7384 | 7761.4998 | 7853.4313 | 7946.5493 | 8040.8701 | 8136.4105 | 8233.1874 | 8331.2181 | 8430.52 | 8531.1109 | 8633.0087 | 8736.2317 | 8840.7984
| Inverter replacement costs | [10 empty] | 48098.3281 | 539.8604 | 546.501 | 553.2298 | 560.0482 | 566.9573 | 573.9584 | 581.0529 | 588.242 | 595.5272 | 602.9098 | 610.3912 | 617.9728 | 625.6561 | 633.4424 | 641.3334 | 649.3304
| Initial CapEx costs | #REF! 2022: #REF!
| Battery replacement costs | #REF! 2042: 149833.0197; #REF! 2043: 4041.3157; #REF! 2044: 4088.4862; #REF! 2045: 4136.2574; #REF! 2046: 4184.6375; #REF! 2047: 4233.6347; #REF! 2048: 4283.2576
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!

## 7 - Cost Benefit - 30% (hidden)
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-1 |  | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 |  | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 |  | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 30% Distributed Energy Storage | Losses (MWh) | 38659.7 | 39104.55 | 39252.8333 | 39104.55 | 39703.4761 | 40302.4022 | 40901.3283 | 41500.2543 | 42099.1804 | 42698.1065 | 43297.0326 | 43895.9587 | 44494.8848 | 45093.8109 | 45692.737 | 46291.663 | 46890.5891 | 47489.5152 | 48088.4413 | 48687.3674 | 49286.2935 | 49885.2196 | 50484.1457 | 51083.0717 | 51681.9978 | 52280.9239 | 52879.85
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3182 | 82.2611 | 155.204 | 228.147 | 301.0899 | 374.0328 | 557.9576 | 741.8825 | 925.8073 | 1109.7321 | 1293.6569 | 1735.8678 | 2178.0788 | 2620.2897
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28719 | 1.5201 | 2.753 | 3.9859 | 5.2187 | 6.4516 | 8.7184 | 10.9851 | 13.2518 | 15.5186 | 17.7853 | 23.9999 | 30.2145 | 36.4292
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66278 | 8.6856 | 16.7085 | 24.7313 | 32.7541 | 40.777 | 78.5603 | 116.3437 | 154.127 | 191.9104 | 229.6938 | 336.053 | 442.4122 | 548.7714
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0082992 | 0.070121 | 0.13194 | 0.19376 | 0.25558 | 0.31741 | 0.48982 | 0.66224 | 0.83466 | 1.0071 | 1.1795 | 1.5853 | 1.991 | 2.3968
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69865 | 3.906 | 7.1133 | 10.3206 | 13.5279 | 16.7352 | 21.9523 | 27.1694 | 32.3865 | 37.6036 | 42.8207 | 53.2304 | 63.6402 | 74.0499
N-1 |  | Available Flex-1 | 8.07 | 213.2596 | 418.4492 | 623.6388 | 828.8285 | 1034.0181 | 1239.2077 | 1444.3973 | 1649.5869 | 1854.7765 | 2059.9662 | 2265.1558 | 2470.3454 | 2675.535 | 2880.7246 | 3085.9142 | 3291.1038 | 3496.2935 | 3701.4831 | 3906.6727 | 4111.8623 | 4317.0519 | 4522.2415 | 4727.4312 | 4932.6208 | 5137.8104 | 5343
N-1 |  | Available Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7984 | 164.8932 | 305.988 | 447.0829 | 588.1777 | 729.2725 | 1026.7866 | 1324.3008 | 1621.8149 | 1919.329 | 2216.8431 | 2851.309 | 3485.7749 | 4120.2408
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7984 | 58.4271 | 93.0558 | 127.6845 | 162.3132 | 196.9419 | 223.8274 | 250.7128 | 277.5982 | 304.4837 | 331.3691 | 350.1626 | 368.9561 | 387.7497
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021739 | 0.95001 | 1.8783 | 2.8066 | 3.7348 | 4.6631 | 9.8055 | 14.9478 | 20.0901 | 25.2325 | 30.3748 | 52.8682 | 75.3617 | 97.8551
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021739 | 0.15062 | 0.27951 | 0.40839 | 0.53727 | 0.66616 | 0.93792 | 1.2097 | 1.4815 | 1.7532 | 2.025 | 2.6045 | 3.1841 | 3.7637
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.2 | 3.4 | 4.6 | 5.8 | 7 | 8.6 | 10.2 | 11.8 | 13.4 | 15 | 18.6667 | 22.3333 | 26
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component |  |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 122489.8233 | Losses (MWh) | 12228.35 | 12380.0038 | 12828.2244 | 13573.0115 | 13570.5893 | 13568.1671 | 13565.7448 | 13563.3226 | 13560.9003 | 13558.4781 | 13556.0559 | 13553.6336 | 13551.2114 | 13548.7891 | 13546.3669 | 13543.9446 | 13541.5224 | 13539.1002 | 13536.6779 | 13534.2557 | 13531.8334 | 13529.4112 | 13526.989 | 13524.5667 | 13522.1445 | 13519.7222 | 13517.3
| 6043531.5976 | Losses ($) | 489134 | 507580.1577 | 539106.1287 | 584665.9552 | 599175.656 | 614045.4257 | 629284.1991 | 644901.1327 | 660905.6104 | 677307.2488 | 694115.9031 | 711341.6731 | 728994.9091 | 747086.2184 | 765626.4714 | 784626.8081 | 804098.6451 | 824053.6822 | 844503.9095 | 865461.6146 | 886939.39 | 908950.1407 | 931507.0918 | 954623.7966 | 978314.1447 | 1002592.3704 | 1027473.061
N-1 | 9289.5531 | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1557.8318 | 1774.1389 | 1990.446 | 2206.753 | 2813.8801 | 3421.0072 | 3917.1524 | 4413.2975 | 4336.8927 | 4947.5479 | 5558.2031 | 5910.5722 | 6262.9412 | 6615.3103
N-1 | 269.7375 | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.0128 | 51.1799 | 54.347 | 57.5141 | 58.2613 | 59.0084 | 58.7216 | 58.4349 | 58.1482 | 67.2814 | 76.4147 | 81.6001 | 86.7855 | 91.9708
N-1 | 1026.7849 | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 110.8049 | 131.4475 | 152.0901 | 172.7327 | 272.845 | 372.9573 | 443.309 | 513.6608 | 584.0125 | 785.4464 | 986.8804 | 1119.7385 | 1252.5966 | 1385.4547
N-1 | 8.1679 | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3875 | 1.5873 | 1.7872 | 1.9871 | 2.4451 | 2.9031 | 3.2505 | 3.5979 | 3.9453 | 4.5065 | 5.0677 | 5.3955 | 5.7233 | 6.0511
N-1 | 710.7684 | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 116.8014 | 123.4274 | 130.0534 | 136.6794 | 144.8721 | 153.0648 | 159.2477 | 165.4306 | 171.6135 | 177.7964 | 183.9793 | 184.9696 | 185.9598 | 186.9501
N-1 | #REF! | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 | #REF! | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 | 20986.4237 | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 3978.6516 | 4416.9401 | 4855.2286 | 5293.5171 | 5981.8223 | 6670.1275 | 7202.0134 | 7733.8992 | 8265.7851 | 8895.231 | 9524.6769 | 9817.171 | 10109.6651 | 10402.1592
N-0 | 1057.9598 | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 211.2016 | 191.5729 | 171.9442 | 152.3155 | 131.3668 | 110.4181 | 97.2126 | 84.0072 | 70.8018 | 56.3563 | 41.9109 | 35.5574 | 29.2039 | 22.8503
N-0 | 1899.1362 | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3392 | 309.81 | 364.2809 | 418.7518 | 548.1823 | 677.6129 | 802.8293 | 928.0458 | 1053.2623 | 1272.3924 | 1491.5224 | 1693.3014 | 1895.0804 | 2096.8594
N-0 | 22.6769 | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2379 | 4.7257 | 5.2134 | 5.7012 | 6.455 | 7.2088 | 7.8197 | 8.4307 | 9.0416 | 9.7564 | 10.4711 | 10.8781 | 11.2851 | 11.6921
N-0 | 291.4772 | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 52 | 56.1333 | 60.2667 | 64.4 | 69.8 | 75.2 | 80.2 | 85.2 | 90.2 | 96.6 | 103 | 107.3333 | 111.6667 | 116
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Project Cost |  | #REF!
Benefit-Cost Ratio |  | #REF!

## 8 - Distributed Storage - 50% (hidden)
10% Distributed Storage
| Equipment Categories All costs are $x1,000 | [6 empty] | Units | kV | Cost | Adjusted Cost
1 | New Substation Equipment
| 500kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 36194.3937 | 0 |  | 0
| 115kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 4403.9172 | 1 |  | 4403.9172
| 230kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 17710.3457 | 0 |  | 0
2 | Transformer Banks
| 500/115 kV 1-3 Phase |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 24748.4568 | 0 |  | 0
| 230/115 kV |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 8756.8817 | 1 |  | 8756.8817
kV
3 | Line Positions to terminate ties and Transformer Bank positions |  |  |  | 230 | 500 | 115
| Single Breaker (add third breaker to breaker and a half) |  |  |  | 2145.4637 | 5398.3718 | 1437.1815 | 0 | 115 | 0
| Breaker and a half (2CB) |  |  |  | 3607.9737 | 8587.7771 | 2149.8636 | 0 | 230 | 0
| Breaker and a half (3CB) |  |  |  | 5291.2883 | 12131.4222 | 3436.5983 | 1 | 115 | 3436.5983
| Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | Used in substation expansion |  | 540.3386 |  | 252.4804 | 0 | 115 | 0
4 | Shunt Capacitors | [5 empty] | 2006.8433 | 0 |  | 0
5 | Fiber optic cable on existing poles | /mile |  |  |  | 99 | 99 | 0 |  | 0
| Fiber optic cable on new poles | /mile |  |  |  | 134 | 134 | 0
6 | Single Circuit, Lattice Tower | /mile |  |  | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
[5 empty] | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
| Double Circuit, Strung on both sides, Lattice Tower | /mile |  |  | 4494.8333 | 9381.7495 | 2174.744
| Rebuild/reconductor existing single circuit line section - Metropolitan | /mile |  |  |  |  | 1381.7727 | 0 |  | 0
| Rebuild/reconductor existing double circuit line section - Metropolitan | /mile |  |  |  |  | 1454.8259 | 0 |  | 0
7 | Disconnect switches (incl. steel structures and foundations) |  |  |  | 3326.9104 | 19935.5969 | 105.461 | 0 | 115 | 0 |  | T&D Costs | 16597.3971
8 | Energy Storage |  |  |  |  | Base price
2024 | Battery Price (Power) | $/kW |  |  |  | 175 | #REF! | 614.4801 |  | #REF!
2024 | Battery Price (Energy) | $/kWh |  |  |  | 310 | #REF! | 1228.9601 |  | #REF!
2024 | Battery Price (Energy uprate) | $/kWh |  |  |  | 310 | #REF! | 1439.9227 |  | #REF!
[12 empty] | ESS-1 | #REF!
2030 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 35.6537 |  | #REF!
2030 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 71.3073 |  | #REF!
2030 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 289.6916 |  | #REF!
[12 empty] | ESS-2 | #REF!
[12 empty] | ESS-2 W escalation | #REF!
2035 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 37.9282 |  | #REF!
2035 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 75.8564 |  | #REF!
2035 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 302.1359 |  | #REF!
2035 | Inverter Replacement | $/kW | [5 empty] | 614.4801 |  | #REF! |  | ESS-3 | #REF!
[12 empty] | ESS-3 W escalation | #REF!
2040 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 40.36 |  | #REF!
2040 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 80.7199 |  | #REF!
2040 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 315.4008 |  | #REF!
2040 | Inverter Replacement | MW | [5 empty] | 35.6537 |  | #REF! |  | ESS-4 | #REF!
2040 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF! |  | ESS-4 W escalation | #REF!
2045 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 25.4529 |  | #REF!
2045 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 50.9059 |  | #REF!
2045 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 290.8851 |  | #REF!
2045 | Inverter Replacement | MW | [5 empty] | 37.9282 |  | #REF!
2045 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF!
[12 empty] | ESS-5 | #REF!
[12 empty] | ESS-5 w escalation | #REF!
| Total Cost | [8 empty] | 516040.796
| Total Cost with Contingency | [8 empty] | #REF!
| Total Cost with SCE Escalation Rate | [8 empty] | #REF!
Factor Amounts: |  |  |  |  | Low Impact factors: |  |  | Medium Impact factors: |  |  | High Impact factors:
| Terrain (CAISO per unit costs) |  |  |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  |  | 2.0X to 3.0X
| Terrain (User specified) |  |  |  |  | 1.25 |  |  | 1.5 |  |  | 2
| Population density (CAISO per unit costs) |  |  |  |  | 1.00X to 1.10X |  |  | 1.33X |  |  | 1.67X
| Population density(User specified) |  |  |  |  | 1.1 |  |  | 1.33 |  |  | 1.67
| Weather study (CAISO per unit costs) |  |  |  |  | 1.35X |  |  | 1.45X |  |  | 1.60X
| Weather study(User specified) |  |  |  |  | 1.35 |  |  | 1.45 |  |  | 1.6
| Factor Type |  |  | Explanation of Factor issues and Factor multipliers
| Terrain |  |  | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
| Population density |  |  | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
| Weather study |  |  | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
[5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2030 and beyond
|  |  |  | Escalation Rate | 2.696% | 2.138% | 2.556% | 2.352% | 2.287% | 2.333% | 2.249% | 2.332% | 2.295% | 2.01% | 2.212% | 0.023
|  |  |  | Escalation Factors | 1 | 1.0214 | 1.0475 | 1.0721 | 1.0966 | 1.1222 | 1.1475 | 1.1742 | 1.2012 | 1.2253 | 1.2524 | 1.2812
| Contingency Factor |  | #REF!
| Contingency Factor for battery | Power | #REF!
|  | Energy | #REF!
Notes
| Contingency Factor included to account for the following considerations |  |  |  | 2018: The SDGE project has been ranked as high impact due to terrain and population, primarily driven by the complications associated with traversing the Pechanga Reservation
o Review of customer/developer existing and proposed plans (i.e. surveyed base map, street/land
improvements, profiles, grading, overhead & underground utilities, temp construction roads &
laydown/staging yards, etc.)
o Property rights study
o Right-of-way improvements/acquisitions (i.e. easements, access/maintenance roads, grading, etc.)
o GO 131-D engineering/permitting per CEQA requirements
o Non-GO 131-D Permitting (i.e. Railroad, City, County, State, Federal Agency, etc.)
o Governing regulation impacts (i.e. CPUC, FERC, OSHA, etc.)
o Environmental study and mitigations
o EMF study and potential reduction mitigations as required by the CPUC
o Geotechnical investigation and mitigations
o Surveys
o Potholing
o Traffic plans/control
o Concrete and/or asphalt repairs
o Associated SCE Substation work (i.e. breaker replacements, switch-rack position relocations, etc.)
o Associated SCE Distribution voltage under-build work (i.e. 16 kV, 12 kV, 4 kV, and secondary
conductors)
o Associated SCE Telecommunication under-build work
o Associated 3rd Party Joint Owners and renters/tenants under-build work (i.e. cable TV,
communication cable, fiber optic, etc.)
o Conflicts associated with other projects in the same geographical area or electrical system
o Availability of line outages required for construction
Unit costs exclude Licensing.
| ESS O&M | #REF! | $/kWh
| + | 1% | of EPC Cost |  | 2020: Add contingency for battery value
| Price Escalation | 2.5% |  |  | 2020: Battery cost reduction = 0%, global factor, and what it changes
| T&D Annual OPEX | #REF! |  |  | 2020: Include 2% into battery price escalation
| Inverter Replacement Cost | #REF! | $/kWh |  | 2020: Make the significant digits, 1000$ of dollars
| Battery Replacement Cost | #REF! | % Capex |  | 2020: shift it to 99 instead of 90, not take actual MW
| Annual Battery Cost Change | #REF!
| Price Stabizes in | #REF!
| Calendar Time (Year) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| O&M T&D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Initial CapEx costs | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| Total Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| MW | 561.8036 | 6.3057 | 6.3833 | 6.4619 | 6.5415 | 6.6222 | 6.704 | 6.7869 | 6.8709 | 6.9559 | 7.0422 | 7.1296 | 7.2181 | 7.3079 | 7.3988 | 7.491 | 7.5844 | 7.679 | 7.775 | 7.8722 | 7.9708 | 8.0706 | 8.1719 | 8.2745 | 8.3784 | 8.4838 | 8.5907
| MWh | 1123.6072 | 12.6115 | 12.7666 | 12.9238 | 13.0831 | 13.2445 | 13.408 | 13.5738 | 13.7417 | 13.9119 | 14.0844 | 14.2591 | 14.4362 | 14.6157 | 14.7976 | 14.982 | 15.1688 | 15.3581 | 15.55 | 15.7444 | 15.9415 | 16.1413 | 16.3437 | 16.5489 | 16.7569 | 16.9677 | 17.1813
| MWh uprate | 1146.0793 | 35.3359 | 35.7463 | 36.162 | 36.5829 | 37.0092 | 37.4409 | 37.8781 | 38.3209 | 38.7693 | 39.2235 | 39.6834 | 40.1493 | 40.6211 | 41.0989 | 41.5829 | 42.0731 | 42.5696 | 43.0725 | 43.5818 | 44.0977 | 44.6203 | 45.1496 | 45.6858 | 46.2289 | 46.779 | 47.3363
| Battery price | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902
| Energy price | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804
| Inverter replacement MW | [10 empty] | 561.8036 | 6.3057 | 6.3833 | 6.4619 | 6.5415 | 6.6222 | 6.704 | 6.7869 | 6.8709 | 6.9559 | 7.0422 | 7.1296 | 7.2181 | 7.3079 | 7.3988 | 7.491 | 7.5844
| Battery costs | 499443.3989 | 13471.0522 | 13628.2875 | 13787.5248 | 13948.7916 | 14112.1156 | 14277.5253 | 14445.0491 | 11916.4406 | 12056.5542 | 12198.4638 | 12342.1943 | 12487.7707 | 12635.2187 | 12784.564 | 12935.8329 | 13089.0522 | 13244.2488 | 13401.4501 | 13560.6841 | 13721.979 | 13885.3635 | 14050.8667 | 14218.5181 | 14388.3478 | 14560.3861 | 14734.664
| Inverter replacement costs | [10 empty] | 80163.8802 | 899.7673 | 910.835 | 922.0497 | 933.4136 | 944.9288 | 956.5973 | 968.4214 | 980.4034 | 992.5454 | 1004.8497 | 1017.3187 | 1029.9547 | 1042.7601 | 1055.7374 | 1068.889 | 1082.2173
| Initial CapEx costs | #REF! 2022: #REF!
| Battery replacement costs | #REF! 2042: 249721.6995; #REF! 2043: 6735.5261; #REF! 2044: 6814.1437; #REF! 2045: 6893.7624; #REF! 2046: 6974.3958; #REF! 2047: 7056.0578; #REF! 2048: 7138.7626
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!

## 8 - Cost Benefit -50% (hidden)
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-1 |  | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 |  | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 |  | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 30% Distributed Energy Storage | Losses (MWh) | 38659.7 | 39104.55 | 39252.8333 | 39104.55 | 39703.4761 | 40302.4022 | 40901.3283 | 41500.2543 | 42099.1804 | 42698.1065 | 43297.0326 | 43895.9587 | 44494.8848 | 45093.8109 | 45692.737 | 46291.663 | 46890.5891 | 47489.5152 | 48088.4413 | 48687.3674 | 49286.2935 | 49885.2196 | 50484.1457 | 51083.0717 | 51681.9978 | 52280.9239 | 52879.85
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395.2673 | 603.5394 | 811.8115 | 1020.0836
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4342 | 8.3501 | 11.266 | 14.1819
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1812 | 118.0001 | 165.8189 | 213.6377
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36038 | 0.55129 | 0.74219 | 0.93309
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.0835 | 18.3316 | 23.5797 | 28.8278
N-1 |  | Available Flex-1 | 8.07 | 430.1827 | 852.2954 | 1274.4081 | 1696.5208 | 2118.6335 | 2540.7462 | 2962.8588 | 3384.9715 | 3807.0842 | 4229.1969 | 4651.3096 | 5073.4223 | 5495.535 | 5917.6477 | 6339.7604 | 6761.8731 | 7183.9858 | 7606.0985 | 8028.2112 | 8450.3238 | 8872.4365 | 9294.5492 | 9716.6619 | 10138.7746 | 10560.8873 | 10983
N-1 |  | Available Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 677.34 | 986.2324 | 1295.1249 | 1604.0173
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.573 | 246.0177 | 284.4623 | 322.907
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7123 | 6.8705 | 10.0286 | 13.1868
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61872 | 0.90088 | 1.183 | 1.4652
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 7 | 8 | 9
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component |  |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 122489.8233 | Losses (MWh) | 12228.35 | 12380.0038 | 12828.2244 | 13573.0115 | 13570.5893 | 13568.1671 | 13565.7448 | 13563.3226 | 13560.9003 | 13558.4781 | 13556.0559 | 13553.6336 | 13551.2114 | 13548.7891 | 13546.3669 | 13543.9446 | 13541.5224 | 13539.1002 | 13536.6779 | 13534.2557 | 13531.8334 | 13529.4112 | 13526.989 | 13524.5667 | 13522.1445 | 13519.7222 | 13517.3
| 6043531.5976 | Losses ($) | 489134 | 507580.1577 | 539106.1287 | 584665.9552 | 599175.656 | 614045.4257 | 629284.1991 | 644901.1327 | 660905.6104 | 677307.2488 | 694115.9031 | 711341.6731 | 728994.9091 | 747086.2184 | 765626.4714 | 784626.8081 | 804098.6451 | 824053.6822 | 844503.9095 | 865461.6146 | 886939.39 | 908950.1407 | 931507.0918 | 954623.7966 | 978314.1447 | 1002592.3704 | 1027473.061
N-1 | 10359.1937 | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6456.5927 | 7042.9006 | 7629.2085 | 8215.5164
N-1 | 285.6848 | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 88.7658 | 97.2499 | 105.734 | 114.2181
N-1 | 1202.9825 | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1146.3929 | 1337.7914 | 1529.1899 | 1720.5884
N-1 | 9.1241 | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 5.8868 | 6.4295 | 6.9722 | 7.5149
N-1 | 748.8102 | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 213.7165 | 219.8684 | 226.0203 | 232.1722
N-1 | #REF! | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 | #REF! | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 | 22861.5769 | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11064.18 | 11682.2476 | 12300.3151 | 12918.3827
N-0 | 1354.5937 | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 165.707 | 139.7023 | 113.6977 | 87.693
N-0 | 1929.4234 | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1518.1849 | 1739.2992 | 1960.4134 | 2181.5277
N-0 | 24.3898 | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 11.8774 | 12.5818 | 13.2862 | 13.9905
N-0 | 306.1976 | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 112 | 119 | 126 | 133
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Project Cost |  | #REF!
Benefit-Cost Ratio |  | #REF!

## Menifee
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Menifee | Losses (MWh) | 49286.625 | 50035.175 | 50580.1202 | 51125.0654 | 51670.0106 | 52214.9558 | 52759.901 | 53304.8462 | 53849.7913 | 54394.7365 | 54939.6817 | 55484.6269 | 56029.5721 | 56574.5173 | 57119.4625 | 57664.4077 | 58209.3529 | 58754.2981 | 59299.2433 | 59844.1885 | 60389.1337 | 60934.0788 | 61479.024 | 62023.9692 | 62568.9144 | 63113.8596 | 63658.8048 | 64203.75
N-1 |  | EENS | 15.9 | 35.4 | 67.2 | 99 | 130.8 | 162.6 | 194.4 | 226.2 | 207.85 | 189.5 | 171.15 | 152.8 | 788.8 | 1054.4 | 1320 | 1585.6 | 1851.2 | 2116.8 | 2595.52 | 3074.24 | 3552.96 | 4031.68 | 4510.4 | 5157.24 | 5804.08 | 6450.92 | 7097.76 | 7744.6
N-1 |  | IP | 5.7 | 11.4 | 14.2333 | 17.0667 | 19.9 | 22.7333 | 25.5667 | 28.4 | 27.4 | 26.4 | 25.4 | 24.4 | 42.4 | 50 | 57.6 | 65.2 | 72.8 | 80.4 | 79.92 | 79.44 | 78.96 | 78.48 | 78 | 91.38 | 104.76 | 118.14 | 131.52 | 144.9
N-1 |  | SAIDI | 0.070196 | 0.19536 | 1.1148 | 2.0343 | 2.9537 | 3.8732 | 4.7927 | 5.7121 | 4.8744 | 4.0366 | 3.1988 | 2.3611 | 35.9821 | 63.9798 | 91.9776 | 119.9754 | 147.9732 | 175.9709 | 252.251 | 328.5311 | 404.8112 | 481.0912 | 557.3713 | 452.852 | 348.3327 | 243.8134 | 139.2941 | 34.7748
N-1 |  | SAIFI | 0.017549 | 0.039071 | 0.074178 | 0.10929 | 0.14439 | 0.1795 | 0.21461 | 0.24971 | 0.22945 | 0.20918 | 0.18891 | 0.16865 | 0.83654 | 1.1046 | 1.3727 | 1.6407 | 1.9088 | 2.1768 | 2.6494 | 3.122 | 3.5945 | 4.0671 | 4.5396 | 3.8491 | 3.1585 | 2.4679 | 1.7773 | 1.0867
N-1 |  | PFD | 4 | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 20.75 | 18.5 | 16.25 | 14 | 44 | 52.4 | 60.8 | 69.2 | 77.6 | 86 | 94.6 | 103.2 | 111.8 | 120.4 | 129 | 138.8 | 148.6 | 158.4 | 168.2 | 178
N-1 |  | Deficit Flex-1 | 4257.2104 | 6452.868 | 8648.5255 | 10844.183 | 13039.8406 | 15235.4981 | 17431.1556 | 19626.8132 | 21822.4707 | 24018.1283 | 26213.7858 | 28409.4433 | 30605.1009 | 32800.7584 | 34996.416 | 37192.0735 | 39387.731 | 41583.3886 | 43779.0461 | 45974.7037 | 48170.3612 | 50366.0187 | 52561.6763 | 54757.3338 | 56952.9913 | 59148.6489 | 61344.3064 | 63539.964
N-1 |  | Deficit Flex-2-1 | 73083.5796 | 75890.6326 | 78697.6855 | 80364.8185 | 82046.2005 | 83713.3335 | 85522.9565 | 87318.3305 | 89113.7045 | 90909.0785 | 92747.1995 | 94585.3205 | 96437.6905 | 98275.8115 | 100056.9365 | 101838.0615 | 103633.4355 | 105414.5605 | 107067.4445 | 108720.3285 | 110373.2125 | 112011.8475 | 113479.4945 | 114932.8924 | 116386.2904 | 117853.9374 | 119093.6004 | 120333.2634
N-1 |  | Deficit Flex-2-2 | 17164.3208 | 19844.0887 | 22754.5274 | 24601.2435 | 26524.5104 | 28541.0948 | 30814.4348 | 33148.2171 | 35561.9498 | 38077.7187 | 40736.7643 | 43501.2116 | 46385.9444 | 49358.9359 | 52298.7216 | 55356.3439 | 58553.2882 | 61842.499 | 65024.8853 | 68293.2688 | 71656.491 | 75060.9515 | 78184.8129 | 81331.7015 | 84513.9878 | 87765.4351 | 90580.7698 | 93440.6833
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2667 | 48.5333 | 72.8 | 141.64 | 210.48 | 279.32 | 348.16 | 417 | 530.52 | 644.04 | 757.56 | 871.08 | 984.6
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6667 | 19.3333 | 29 | 39.76 | 50.52 | 61.28 | 72.04 | 82.8 | 92.24 | 101.68 | 111.12 | 120.56 | 130
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1607 | 0.3214 | 0.4821 | 1.9505 | 3.4189 | 4.8874 | 6.3558 | 7.8242 | 13.2143 | 18.6045 | 23.9946 | 29.3847 | 34.7748
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026783 | 0.053567 | 0.08035 | 0.15633 | 0.23231 | 0.30829 | 0.38427 | 0.46025 | 0.58554 | 0.71083 | 0.83613 | 0.96142 | 1.0867
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3333 | 2.6667 | 4 | 4.8 | 5.6 | 6.4 | 7.2 | 8 | 9.2 | 10.4 | 11.6 | 12.8 | 14
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91213.7868 | 376966.3176 | 785798.4559 | 1317282.83 | 1885288.5255 | 2201307.1349 | 3051349.419 | 3895785.7558 | 4575658.7644 | 5166780.0228 | 6360287.9131 | 7438141.0568 | 8727913.0099
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 513985.547 | 2124188.0835 | 4166493.7975 | 7009579.1683 | 9899371.7464 | 10518234.1258 | 14704076.305 | 18976439.3542 | 21500874.7537 | 22954815.5749 | 28543787.9835 | 32989589.6503 | 38556566.6396
N-1 Monetized | Residential | $ | 3395.2945 | 11092.4682 | 18789.6419 | 26486.8156 | 34183.9893 | 41881.163 | 49578.3367 | 57275.5104 | 92690.4946 | 128105.4788 | 163520.4631 | 198935.4473 | 309530.5235 | 420125.5997 | 530720.6758 | 641315.752 | 751910.8282 | 862505.9044 | 1128286.7009 | 1394067.4975 | 1659848.2941 | 1925629.0906 | 2191409.8872 | 2624954.9121 | 3058499.9371 | 3492044.962 | 3925589.9869 | 4359135.0119
N-1 Monetized | Commercial | $ | 14088.7262 | 21785.8999 | 29483.0736 | 37180.2473 | 44877.421 | 52574.5947 | 60271.7684 | 237663.9186 | 384617.8938 | 531571.8691 | 678525.8443 | 825479.8195 | 1284392.5209 | 1743305.2222 | 2202217.9235 | 2661130.6249 | 3120043.3262 | 3578956.0275 | 4681809.6765 | 5784663.3255 | 6887516.9745 | 7990370.6234 | 9093224.2724 | 10892213.2096 | 12691202.1468 | 14490191.0839 | 16289180.0211 | 18088168.9583
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5110374.2214 | 6015097.5811 | 6967510.5921 | 7745187.9968 | 8491036.7137 | 9233048.7464 | 10172667.8173 | 11216525.0586 | 12260160.0595 | 13330830.0069 | 14604368.7155 | 15898045.9904 | 17328004.7347 | 18766389.6983 | 20232001.0865 | 21817429.4974 | 23600568.0435 | 25503802.0729 | 27434997.0562 | 29443388.6443 | 31566313.1487 | 33843442.2534 | 36000441.2918 | 38358137.1162 | 40806428.0067 | 43292848.4471 | 45372446.2399 | 47951699.3087
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 11249.1458 | Losses (MWh) | 795.125 | 852.875 | 904.4337 | 955.9923 | 1007.551 | 1059.1096 | 1110.6683 | 1162.2269 | 1213.7856 | 1265.3442 | 1316.9029 | 1368.4615 | 1420.0202 | 1471.5788 | 1523.1375 | 1574.6962 | 1626.2548 | 1677.8135 | 1729.3721 | 1780.9308 | 1832.4894 | 1884.0481 | 1935.6067 | 1987.1654 | 2038.724 | 2090.2827 | 2141.8413 | 2193.4
| 585160.8729 | Losses ($) | 31805 | 34967.875 | 38008.8243 | 41179.9661 | 44485.9096 | 47931.4127 | 51521.3873 | 55260.9034 | 59155.1946 | 63209.6622 | 67429.8812 | 71821.6051 | 76390.7715 | 81143.5077 | 86086.1365 | 91225.1821 | 96567.3761 | 102119.6641 | 107889.2118 | 113883.4122 | 120109.8918 | 126576.5183 | 133291.4074 | 140262.9306 | 147499.7229 | 155010.6904 | 162805.0191 | 170892.1824
N-1 | 1889.9754 | EENS | 2.1 | 4.6 | 4.6333 | 4.6667 | 4.7 | 4.7333 | 4.7667 | 4.8 | 140.25 | 275.7 | 411.15 | 546.6 | 199.85 | 223.5 | 247.15 | 270.8 | 294.45 | 318.1 | 519.45 | 720.8 | 922.15 | 1123.5 | 752.3 | 900.04 | 1047.78 | 1195.52 | 1343.26 | 1491
N-1 | -46.1734 | IP | -2.2 | -5.4 | -5.35 | -5.3 | -5.25 | -5.2 | -5.15 | -5.1 | -1.15 | 2.8 | 6.75 | 10.7 | -2.9 | -6.1 | -9.3 | -12.5 | -15.7 | -18.9 | -16.44 | -13.98 | -11.52 | -9.06 | -6.6 | -8.58 | -10.56 | -12.54 | -14.52 | -16.5
N-1 | 606.4801 | SAIDI | 0.1332 | 0.26069 | 0.017575 | -0.22554 | -0.46865 | -0.71176 | -0.95487 | -1.198 | 4.8791 | 10.9561 | 17.0332 | 23.1103 | 18.1547 | 18.8224 | 19.4901 | 20.1577 | 20.8254 | 21.4931 | 53.3481 | 85.2031 | 117.0582 | 148.9132 | 180.7682 | 524.5048 | 868.2414 | 1211.978 | 1555.7147 | 1899.4513
N-1 | 2.1362 | SAIFI | -0.0035432 | -0.0081483 | -0.016587 | -0.025026 | -0.033466 | -0.041905 | -0.050344 | -0.058783 | 0.066428 | 0.19164 | 0.31685 | 0.44206 | 0.035852 | 0.029482 | 0.023111 | 0.016741 | 0.010371 | 0.0040003 | 0.051267 | 0.098534 | 0.1458 | 0.19307 | 0.24033 | 1.6645 | 3.0887 | 4.5129 | 5.9371 | 7.3613
N-1 | 388.6179 | PFD | 14 | 23 | 25.3333 | 27.6667 | 30 | 32.3333 | 34.6667 | 37 | 46.25 | 55.5 | 64.75 | 74 | 53.8333 | 55.2667 | 56.7 | 58.1333 | 59.5667 | 61 | 63.8 | 66.6 | 69.4 | 72.2 | 75 | 76.6 | 78.2 | 79.8 | 81.4 | 83
N-1 | 97911.486 | Flex-1 | 2069.8236 | 3137.6992 | 4205.5748 | 5273.4505 | 6341.3261 | 7409.2017 | 8477.0774 | 9544.953 | 10612.8286 | 11680.7043 | 12748.5799 | 13816.4555 | 14884.3311 | 15952.2068 | 17020.0824 | 18087.958 | 19155.8337 | 20223.7093 | 21291.5849 | 22359.4606 | 23427.3362 | 24495.2118 | 25563.0875 | 26630.9631 | 27698.8387 | 28766.7144 | 29834.59 | 30902.4656
N-1 | 1159523.3929 | Flex-2-1 | 121528.9563 | 122079.0547 | 122629.1532 | 122955.8614 | 123285.362 | 123612.0702 | 123966.7022 | 124318.5419 | 124670.3815 | 125022.2211 | 125382.4379 | 125742.6546 | 126105.6638 | 126465.8805 | 126814.9278 | 127163.975 | 127515.8146 | 127864.8619 | 128188.7777 | 128512.6936 | 128836.6094 | 129157.7329 | 129445.3478 | 129730.1703 | 130014.9929 | 130302.6078 | 130545.5447 | 130788.4816
| 625479.561 | Flex-2-2 | 43849.6441 | 47666.1912 | 51623.0473 | 54016.9826 | 56464.4711 | 58848.3085 | 61506.8809 | 64212.3112 | 66996.4044 | 69825.2804 | 72773.518 | 75714.333 | 78717.3741 | 81702.7173 | 84628.6566 | 87572.1253 | 90542.9416 | 93513.3844 | 96262.8354 | 99037.2825 | 101828.9405 | 104676.614 | 107213.1187 | 109729.1881 | 112291.2474 | 114921.1958 | 117146.0692 | 119382.045
N-0 | 20662.7139 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4557.5667 | 5112.6833 | 5667.8 | 6428.36 | 7188.92 | 7949.48 | 8710.04 | 9470.6 | 10284.04 | 11097.48 | 11910.92 | 12724.36 | 13537.8
N-0 | 1237.886 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 240.3333 | 245.6667 | 251 | 253.92 | 256.84 | 259.76 | 262.68 | 265.6 | 268.6 | 271.6 | 274.6 | 277.6 | 280.6
N-0 | 1743.7602 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.5993 | 365.8378 | 421.0762 | 549.9666 | 678.857 | 807.7474 | 936.6378 | 1065.5282 | 1284.4105 | 1503.2928 | 1722.1751 | 1941.0574 | 2159.9396
N-0 | 21.9701 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8495 | 5.4394 | 6.0292 | 6.8359 | 7.6426 | 8.4494 | 9.2561 | 10.0628 | 10.9241 | 11.7853 | 12.6465 | 13.5078 | 14.369
N-0 | 273.7617 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 57 | 61 | 65 | 70.8 | 76.6 | 82.4 | 88.2 | 94 | 100.8 | 107.6 | 114.4 | 121.2 | 128
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 989522.6961 | -731.1221 | -4395.8117 | -3493.4999 | -2591.1881 | -1688.8764 | -786.5646 | 115.7471 | 1018.0589 | 13164.4288 | 25310.7988 | 37457.1687 | 49603.5386 | 83007.132 | 116410.7253 | 149814.3187 | 183217.912 | 216621.5054 | 250025.0987 | 328665.7958 | 407306.4928 | 485947.1899 | 564587.887 | 643228.584 | 763585.3579 | 883942.1318 | 1004298.9057 | 1124655.6795 | 1245012.4534
Commerical(N-1) | EENS | 4415415.7379 | -3033.7808 | 6001.7813 | 33988.0506 | 61974.32 | 89960.5893 | 117946.8587 | 145933.128 | 4224.4209 | 54625.6108 | 105026.8008 | 155427.9907 | 205829.1807 | 344436.9179 | 483044.6551 | 621652.3923 | 760260.1296 | 898867.8668 | 1037475.604 | 1363794.062 | 1690112.5201 | 2016430.9781 | 2342749.4361 | 2669067.8941 | 3168486.6218 | 3667905.3494 | 4167324.077 | 4666742.8047 | 5166161.5323
Aggregate | EENS | 5404938.434 | -3764.9029 | 1605.9696 | 30494.5507 | 59383.1318 | 88271.7129 | 117160.294 | 146048.8751 | 5242.4797 | 67790.0396 | 130337.5995 | 192885.1594 | 255432.7193 | 427444.0499 | 599455.3805 | 771466.711 | 943478.0416 | 1115489.3721 | 1287500.7027 | 1692459.8578 | 2097419.0129 | 2502378.168 | 2907337.3231 | 3312296.4782 | 3932071.9797 | 4551847.4812 | 5171622.9827 | 5791398.4842 | 6411173.9857
Residential (N-0) | EENS | 117915945.3374 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17866466.9567 | 20996797.7861 | 24606885.2014 | 28463351.0241 | 32755418.8975 | 37153791.2979 | 42652806.9717 | 47863840.3196 | 52976261.7995 | 58057231.1711 | 63616417.7284 | 70586796.032 | 77712608.8621 | 82858013.6784 | 91213408.9156
Commerical(N-0) | EENS | 503557592.8294 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 77675195.1106 | 90392543.5661 | 106180983.2088 | 122221178.0273 | 139545937.7145 | 157548767.2612 | 180833131.6234 | 201218261.6304 | 222936793.9859 | 242047844.0782 | 263909953.9314 | 293434496.7769 | 322983031.4839 | 339046590.7163 | 366596418.9225
Aggregate | EENS | 621473538.1669 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 95541662.0673 | 111389341.3522 | 130787868.4103 | 150684529.0514 | 172301356.612 | 194702558.5591 | 223485938.5952 | 249082101.95 | 275913055.7854 | 300105075.2493 | 327526371.6598 | 364021292.8089 | 400695640.346 | 421904604.3947 | 457809827.8381
Residential (N-1) | Value for Flex-1 | 537491839.018 | 8166198.0825 | 12688835.1743 | 17432500.2468 | 22405418.051 | 27616086.4327 | 33073284.8472 | 38786083.1285 | 44763850.5207 | 51016264.9807 | 57553322.757 | 64385348.2566 | 71523004.2044 | 78977302.1069 | 86759613.027 | 94881678.6792 | 103355622.8559 | 112193963.1923 | 121409623.2812 | 131015945.1475 | 141026702.0926 | 151456111.9193 | 162318850.5484 | 173630066.0391 | 185405393.0227 | 197660967.5643 | 210413442.4622 | 223680003.0004 | 237478383.1639
Commerical(N-1) | Value for Flex-1 | 2214268856.2862 | 33641735.1404 | 52273337.9547 | 71815494.8253 | 92302088.7032 | 113768127.5908 | 136249779.6173 | 159784409.1653 | 184410614.0786 | 210168263.9817 | 237098539.7462 | 265243974.1339 | 294648493.6537 | 325357461.6657 | 357417722.7697 | 390877648.5153 | 425787184.4715 | 462197898.6952 | 500163031.6398 | 539737547.545 | 580978187.3506 | 623943523.1793 | 668694014.4323 | 715292065.546 | 763802085.4563 | 814290548.8212 | 866826059.051 | 921479413.1992 | 978323668.7679
Aggregate | Value for Flex-1 | 2751760695.3042 | 41807933.2229 | 64962173.129 | 89247995.0721 | 114707506.7542 | 141384214.0235 | 169323064.4645 | 198570492.2938 | 229174464.5993 | 261184528.9624 | 294651862.5032 | 329629322.3905 | 366171497.8581 | 404334763.7726 | 444177335.7966 | 485759327.1945 | 529142807.3274 | 574391861.8875 | 621572654.921 | 670753492.6925 | 722004889.4432 | 775399635.0985 | 831012864.9807 | 888922131.5851 | 949207478.479 | 1011951516.3855 | 1077239501.5132 | 1145159416.1995 | 1215802051.9317
Residential (N-1) | Value for Flex-2 | 47821744.8976 | 4046381.8903 | 4166315.2033 | 4289716.1932 | 4408673.4632 | 4531000.15 | 4656582.5587 | 4786690.4255 | 4920282.8048 | 5057563.1215 | 5198632.2774 | 5343950.9576 | 5493286.4267 | 5646873.7394 | 5804578.9482 | 5966114.6423 | 6132099.2593 | 6302792.3058 | 6478045.9718 | 6656818.0071 | 6840479.8654 | 7029164.3054 | 7222851.5101 | 7419909.1118 | 7622141.2485 | 7829847.5488 | 8043347.6944 | 8259802.349 | 8482052.644
Commerical(N-1) | Value for Flex-2 | 215563781.8508 | 18239681.2363 | 18780298.8687 | 19336547.582 | 19872765.5528 | 20424171.6814 | 20990253.4714 | 21576734.4517 | 22178922.4013 | 22797734.2894 | 23433624.9453 | 24088670.9782 | 24761823.2972 | 25454141.4479 | 26165021.6406 | 26893168.3278 | 27641369.2108 | 28410794.0555 | 29200776.5853 | 30006618.6996 | 30834502.4343 | 31685026.219 | 32558100.7259 | 33446367.8092 | 34357959.8955 | 35294227.6062 | 36256611.9548 | 37232314.2014 | 38234141.1779
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 263385526.7485 | 22286063.1266 | 22946614.072 | 23626263.7752 | 24281439.016 | 24955171.8314 | 25646836.0301 | 26363424.8773 | 27099205.2061 | 27855297.4109 | 28632257.2227 | 29432621.9358 | 30255109.7238 | 31101015.1873 | 31969600.5888 | 32859282.9701 | 33773468.4701 | 34713586.3614 | 35678822.5571 | 36663436.7067 | 37674982.2997 | 38714190.5244 | 39780952.236 | 40866276.9209 | 41980101.1439 | 43124075.155 | 44299959.6493 | 45492116.5504 | 46716193.8219
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 201421523.7425 | 11415404.7265 | 12677256.0862 | 14005928.335 | 14898443.9956 | 16001404.1511 | 17079540.6575 | 18025564.8207 | 19173409.5383 | 20408716.3778 | 21700257.5548 | 23225050.5217 | 24562337.3095 | 26000278.4294 | 27628571.2119 | 29216356.1057 | 31019684.7629 | 32721790.7961 | 34498473.5373 | 36216597.8881 | 38085174.9541 | 39829235.0504 | 41537971.8595 | 43666848.8026 | 45674640.5094 | 47592810.1302 | 49813062.131 | 52005419.7536 | 54190723.0631
Aggregate ($M) |  | 3843.4462 | 77444176.2155 | 105681495.1015 | 134651824.2658 | 164748534.624 | 195411321.7077 | 226798312.5944 | 262634221.8896 | 299600026.2046 | 339871386.1943 | 385460087.6786 | 435426483.0782 | 489585200.7254 | 545847909.4666 | 599916625.0451 | 659995774.3336 | 725667307.0123 | 793627257.4686 | 865338808.33 | 940028545.7042 | 1023348404.305 | 1105527540.7913 | 1191152182.1847 | 1276872629.0361 | 1368320663.7719 | 1471241541.9607 | 1577219786.6222 | 1670352955.3824 | 1780929970.6405
Aggregate ($M)+ Monetized Losses |  | 3844.0314 | 77475981.2155 | 105716462.9765 | 134689833.0901 | 164789714.5902 | 195455807.6173 | 226846244.0071 | 262685743.2769 | 299655287.108 | 339930541.3889 | 385523297.3408 | 435493912.9593 | 489657022.3305 | 545924300.2381 | 599997768.5528 | 660081860.4701 | 725758532.1944 | 793723824.8447 | 865440927.9941 | 940136434.916 | 1023462287.7172 | 1105647650.6831 | 1191278758.7029 | 1277005920.4435 | 1368460926.7025 | 1471389041.6836 | 1577374797.3127 | 1670515760.4015 | 1781100862.8229
Project Cost |  | 315
Benefit-Cost Ratio |  | 12.2033

## Mira Loma
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Mira Loma | Losses (MWh) | 48849.325 | 49618.5 | 50182.2596 | 50746.0192 | 51309.7788 | 51873.5385 | 52437.2981 | 53001.0577 | 53564.8173 | 54128.5769 | 54692.3365 | 55256.0962 | 55819.8558 | 56383.6154 | 56947.375 | 57511.1346 | 58074.8942 | 58638.6538 | 59202.4135 | 59766.1731 | 60329.9327 | 60893.6923 | 61457.4519 | 62021.2115 | 62584.9712 | 63148.7308 | 63712.4904 | 64276.25
N-1 |  | EENS | 1.3 | 10.6 | 33.1667 | 55.7333 | 78.3 | 100.8667 | 123.4333 | 146 | 231.95 | 317.9 | 403.85 | 489.8 | 693.9833 | 898.1667 | 1102.35 | 1306.5333 | 1510.7167 | 1714.9 | 2202.02 | 2689.14 | 3176.26 | 3663.38 | 4150.5 | 4763.52 | 5376.54 | 5989.56 | 6602.58 | 7215.6
N-1 |  | IP | 1.2 | 4.4 | 7.3667 | 10.3333 | 13.3 | 16.2667 | 19.2333 | 22.2 | 24.95 | 27.7 | 30.45 | 33.2 | 36 | 38.8 | 41.6 | 44.4 | 47.2 | 50 | 53.52 | 57.04 | 60.56 | 64.08 | 67.6 | 78.14 | 88.68 | 99.22 | 109.76 | 120.3
N-1 |  | SAIDI | 0.0026789 | 0.043686 | 0.34026 | 0.63684 | 0.93342 | 1.23 | 1.5266 | 1.8232 | 4.4506 | 7.078 | 9.7054 | 12.3328 | 25.6225 | 38.9123 | 52.202 | 65.4918 | 78.7815 | 92.0713 | 140.7757 | 189.4802 | 238.1846 | 286.8891 | 335.5936 | 439.5996 | 543.6056 | 647.6116 | 751.6176 | 855.6236
N-1 |  | SAIFI | 0.0013394 | 0.010921 | 0.034174 | 0.057426 | 0.080678 | 0.10393 | 0.12718 | 0.15043 | 0.23675 | 0.32306 | 0.40937 | 0.49568 | 0.68848 | 0.88127 | 1.0741 | 1.2669 | 1.4597 | 1.6525 | 2.0736 | 2.4948 | 2.916 | 3.3371 | 3.7583 | 4.2914 | 4.8246 | 5.3577 | 5.8909 | 6.424
N-1 |  | PFD | 2 | 4 | 5.5 | 7 | 8.5 | 10 | 11.5 | 13 | 17.5 | 22 | 26.5 | 31 | 37 | 43 | 49 | 55 | 61 | 67 | 75 | 83 | 91 | 99 | 107 | 116.2 | 125.4 | 134.6 | 143.8 | 153
N-1 |  | Deficit Flex-1 | 3291.5996 | 4989.5231 | 6687.4467 | 8385.3703 | 10083.2938 | 11781.2174 | 13479.141 | 15177.0645 | 16874.9881 | 18572.9116 | 20270.8352 | 21968.7588 | 23666.6823 | 25364.6059 | 27062.5295 | 28760.453 | 30458.3766 | 32156.3002 | 33854.2237 | 35552.1473 | 37250.0708 | 38947.9944 | 40645.918 | 42343.8415 | 44041.7651 | 45739.6887 | 47437.6122 | 49135.5358
N-1 |  | Deficit Flex-2-1 | 141086.1703 | 144165.8249 | 147245.4795 | 149074.5129 | 150919.1791 | 152748.2126 | 154733.5737 | 156703.302 | 158673.0303 | 160642.7586 | 162659.3853 | 164676.0119 | 166708.2713 | 168724.8979 | 170678.9934 | 172633.089 | 174602.8173 | 176556.9129 | 178370.3136 | 180183.7142 | 181997.1149 | 183794.8828 | 185405.0576 | 186999.5995 | 188594.1415 | 190204.3163 | 191564.3668 | 192924.4173
N-1 |  | Deficit Flex-2-2 | 19646.6116 | 22588.9977 | 25771.7274 | 27776.2169 | 29895.4423 | 32061.7027 | 34501.4657 | 37006.1427 | 39617.2378 | 42313.5335 | 45181.1572 | 48158.5713 | 51239.6044 | 54403.942 | 57586.5974 | 60893.483 | 64371.6355 | 67934.9543 | 71344.4987 | 74826.8176 | 78401.2712 | 82012.1325 | 85283.8868 | 88583.2554 | 91951.2051 | 95425.7618 | 98417.9501 | 101462.7804
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 35.4667 | 70.9333 | 106.4 | 189.45 | 272.5 | 355.55 | 438.6 | 606.9667 | 775.3333 | 943.7 | 1112.0667 | 1280.4333 | 1448.8 | 1835.36 | 2221.92 | 2608.48 | 2995.04 | 3381.6 | 3704.08 | 4026.56 | 4349.04 | 4671.52 | 4994
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 12.5333 | 25.0667 | 37.6 | 50.9 | 64.2 | 77.5 | 90.8 | 104.3667 | 117.9333 | 131.5 | 145.0667 | 158.6333 | 172.2 | 185.44 | 198.68 | 211.92 | 225.16 | 238.4 | 249.6 | 260.8 | 272 | 283.2 | 294.4
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0.14095 | 0.28189 | 0.42284 | 1.2976 | 2.1723 | 3.0471 | 3.9218 | 10.2253 | 16.5288 | 22.8323 | 29.1358 | 35.4393 | 41.7428 | 66.3191 | 90.8953 | 115.4716 | 140.0479 | 164.6241 | 220.0162 | 275.4083 | 330.8003 | 386.1924 | 441.5844
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0.035237 | 0.070473 | 0.10571 | 0.18822 | 0.27073 | 0.35324 | 0.43576 | 0.60303 | 0.77031 | 0.93758 | 1.1049 | 1.2721 | 1.4394 | 1.8235 | 2.2075 | 2.5916 | 2.9756 | 3.3597 | 3.6801 | 4.0005 | 4.3208 | 4.6412 | 4.9616
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 1.3333 | 2.6667 | 4 | 5.25 | 6.5 | 7.75 | 9 | 12.3333 | 15.6667 | 19 | 22.3333 | 25.6667 | 29 | 32.2 | 35.4 | 38.6 | 41.8 | 45 | 49.8 | 54.6 | 59.4 | 64.2 | 69
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 155244.8763 | 373501.1933 | 772686.7337 | 1181656.6322 | 1457630.9743 | 2096309.9731 | 2658667.1584 | 3202186.432 | 4124056.9326 | 5158728.3964 | 6679651.5667 | 8344615.2825 | 10723281.6518 | 13320875.8585 | 16346046.8763 | 20018970.7389 | 22101600.8785 | 25698955.9278 | 29122131.301 | 33099323.792 | 37512392.5597 | 42221990.2679 | 46965775.4737
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 874797.8292 | 1957090.9642 | 4109890.3922 | 6196927.7149 | 6925526.0451 | 10174783.5899 | 12390790.2386 | 14100054.1568 | 18126611.8301 | 22205223.0475 | 28653538.7896 | 36255343.1333 | 46800330.6926 | 58871468.859 | 73215327.2361 | 91004698.9148 | 95792356.6273 | 112187663.0536 | 125832754.1411 | 143171093.5195 | 161726450.0425 | 181975313.7887 | 201986788.2441
N-1 Monetized | Residential | $ | 277.6027 | 6735.5414 | 13193.4801 | 19651.4188 | 26109.3575 | 32567.2962 | 39025.2349 | 45483.1736 | 95935.9164 | 146388.6592 | 196841.402 | 180982.7073 | 297746.8876 | 414511.0679 | 531275.2482 | 648039.4284 | 764803.6087 | 881567.789 | 1189910.7692 | 1498253.7493 | 1806596.7294 | 2114939.7096 | 2423282.6897 | 2888666.1913 | 3354049.6929 | 3819433.1946 | 4284816.6962 | 4750200.1978
N-1 Monetized | Commercial | $ | 1151.9084 | 27949.0335 | 54746.1586 | 81543.2837 | 108340.4089 | 135137.534 | 161934.6591 | 188731.7842 | 398084.7255 | 607437.6668 | 816790.608 | 750985.1792 | 1235496.4906 | 1720007.8021 | 2204519.1135 | 2689030.4249 | 3173541.7364 | 3658053.0478 | 4937517.8743 | 6216982.7009 | 7496447.5274 | 8775912.3539 | 10055377.1805 | 11986479.4254 | 13917581.6704 | 15848683.9154 | 17779786.1604 | 19710888.4053
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5799348.3161 | 6749515.6315 | 7911536.0081 | 8597773.9763 | 9445306.7755 | 10346308.0212 | 11371463.4842 | 12358291.3553 | 13547148.5583 | 14761620.3982 | 16103849.337 | 17426439.1394 | 18990300.6754 | 20403201.7509 | 22108987.9525 | 23881494.2434 | 25840240.9361 | 27857739.0476 | 29974240.0835 | 32101550.6843 | 34350839.9935 | 36790442.644 | 39204453.3272 | 41511855.6532 | 43789887.2929 | 46537906.5013 | 49160795.5084 | 51784924.6969
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 13918.0297 | Losses (MWh) | 1232.425 | 1269.55 | 1302.2942 | 1335.0385 | 1367.7827 | 1400.5269 | 1433.2712 | 1466.0154 | 1498.7596 | 1531.5038 | 1564.2481 | 1596.9923 | 1629.7365 | 1662.4808 | 1695.225 | 1727.9692 | 1760.7135 | 1793.4577 | 1826.2019 | 1858.9462 | 1891.6904 | 1924.4346 | 1957.1788 | 1989.9231 | 2022.6673 | 2055.4115 | 2088.1558 | 2120.9
| 706079.488 | Losses ($) | 49297 | 52051.55 | 54728.915 | 57507.6161 | 60391.0467 | 63382.7065 | 66486.2049 | 69705.2641 | 73043.7223 | 76505.5377 | 80094.7915 | 83815.692 | 87672.5783 | 91669.9241 | 95812.3418 | 100104.5867 | 104551.5612 | 109158.319 | 113930.07 | 118872.1846 | 123990.1986 | 129289.8182 | 134776.9249 | 140457.5808 | 146338.0339 | 152424.7237 | 158724.2867 | 165243.5624
N-1 | 2643.0908 | EENS | 16.7 | 29.4 | 38.6667 | 47.9333 | 57.2 | 66.4667 | 75.7333 | 85 | 116.15 | 147.3 | 178.45 | 209.6 | 294.6667 | 379.7333 | 464.8 | 549.8667 | 634.9333 | 720 | 912.95 | 1105.9 | 1298.85 | 1491.8 | 1112.2 | 1293.76 | 1475.32 | 1656.88 | 1838.44 | 2020
N-1 | 27.8523 | IP | 2.3 | 1.6 | 1.5167 | 1.4333 | 1.35 | 1.2667 | 1.1833 | 1.1 | 1.3 | 1.5 | 1.7 | 1.9 | 3.5 | 5.1 | 6.7 | 8.3 | 9.9 | 11.5 | 9.96 | 8.42 | 6.88 | 5.34 | 3.8 | 4.66 | 5.52 | 6.38 | 7.24 | 8.1
N-1 | 623.6015 | SAIDI | 0.20072 | 0.41236 | 0.79213 | 1.1719 | 1.5517 | 1.9315 | 2.3112 | 2.691 | 5.3029 | 7.9148 | 10.5267 | 13.1386 | 28.5143 | 43.89 | 59.2657 | 74.6414 | 90.0171 | 105.3928 | 164.8234 | 224.2541 | 283.6847 | 343.1153 | 402.546 | 537.7573 | 672.9686 | 808.1799 | 943.3912 | 1078.6025
N-1 | 1.9533 | SAIFI | 0.012666 | 0.020002 | 0.023417 | 0.026833 | 0.030248 | 0.033664 | 0.037079 | 0.040495 | 0.059128 | 0.077761 | 0.096394 | 0.11503 | 0.18392 | 0.25281 | 0.32171 | 0.3906 | 0.45949 | 0.52838 | 0.62704 | 0.7257 | 0.82436 | 0.92302 | 1.0217 | 1.2221 | 1.4226 | 1.623 | 1.8235 | 2.024
N-1 | 444.5369 | PFD | 16 | 24 | 27.8333 | 31.6667 | 35.5 | 39.3333 | 43.1667 | 47 | 49.5 | 52 | 54.5 | 57 | 60.8333 | 64.6667 | 68.5 | 72.3333 | 76.1667 | 80 | 83.4 | 86.8 | 90.2 | 93.6 | 97 | 99.2 | 101.4 | 103.6 | 105.8 | 108
N-1 | 143555.8795 | Flex-1 | 3035.4344 | 4601.044 | 6166.6536 | 7732.2632 | 9297.8728 | 10863.4824 | 12429.092 | 13994.7017 | 15560.3113 | 17125.9209 | 18691.5305 | 20257.1401 | 21822.7497 | 23388.3593 | 24953.9689 | 26519.5785 | 28085.1881 | 29650.7977 | 31216.4073 | 32782.0169 | 34347.6266 | 35913.2362 | 37478.8458 | 39044.4554 | 40610.065 | 42175.6746 | 43741.2842 | 45306.8938
N-1 | 512526.5558 | Flex-2-1 | 53526.3656 | 53803.8624 | 54081.3592 | 54246.167 | 54412.3834 | 54577.1912 | 54756.0851 | 54933.5704 | 55111.0557 | 55288.541 | 55470.2521 | 55651.9632 | 55835.083 | 56016.7941 | 56192.8708 | 56368.9475 | 56546.4328 | 56722.5095 | 56885.9086 | 57049.3078 | 57212.7069 | 57374.6975 | 57519.7847 | 57663.4632 | 57807.1418 | 57952.229 | 58074.7784 | 58197.3277
N-1 | 587117.8253 | Flex-2-2 | 41367.3533 | 44921.2822 | 48605.8473 | 50842.0091 | 53093.5392 | 55327.7006 | 57819.85 | 60354.3856 | 62941.1165 | 65589.4656 | 68329.125 | 71056.9733 | 73863.7141 | 76657.7112 | 79340.7808 | 82034.9862 | 84724.5943 | 87420.9291 | 89943.222 | 92503.7337 | 95084.1603 | 97725.433 | 100114.0448 | 102477.6341 | 104854.0301 | 107260.8691 | 109308.889 | 111359.9479
N-0 | 14173.305 | EENS | 48.5 | 118.4 | 225.5833 | 332.7667 | 439.95 | 547.1333 | 654.3167 | 761.5 | 1014.75 | 1268 | 1521.25 | 1774.5 | 2149.7 | 2524.9 | 2900.1 | 3275.3 | 3650.5 | 4025.7 | 4367.98 | 4710.26 | 5052.54 | 5394.82 | 5737.1 | 6051.04 | 6364.98 | 6678.92 | 6992.86 | 7306.8
N-0 | 727.3796 | IP | 21.2 | 37.8 | 49.7 | 61.6 | 73.5 | 85.4 | 97.3 | 93.8 | 95.15 | 96.5 | 97.85 | 99.2 | 100.6333 | 102.0667 | 103.5 | 104.9333 | 106.3667 | 107.8 | 108.24 | 108.68 | 109.12 | 109.56 | 110 | 111.24 | 112.48 | 113.72 | 114.96 | 116.2
N-0 | 1505.3441 | SAIDI | 0.20932 | 0.64277 | 3.2902 | 5.9377 | 8.5851 | 11.2326 | 13.88 | 17.9278 | 34.7563 | 51.5847 | 68.4132 | 85.2417 | 134.3373 | 183.4329 | 232.5286 | 281.6242 | 330.7199 | 379.8155 | 485.5981 | 591.3806 | 697.1632 | 802.9457 | 908.7283 | 1077.6086 | 1246.489 | 1415.3693 | 1584.2497 | 1753.13
N-0 | 16.9262 | SAIFI | 0.051661 | 0.12637 | 0.24121 | 0.35604 | 0.47088 | 0.58572 | 0.70055 | 0.86011 | 1.1386 | 1.4171 | 1.6956 | 1.9741 | 2.4234 | 2.8728 | 3.3221 | 3.7714 | 4.2208 | 4.6701 | 5.1688 | 5.6674 | 6.1661 | 6.6647 | 7.1634 | 7.8295 | 8.4957 | 9.1618 | 9.828 | 10.4941
N-0 | 163.2642 | PFD | 2 | 1 | 1.8333 | 2.6667 | 3.5 | 4.3333 | 5.1667 | 15 | 18.25 | 21.5 | 24.75 | 28 | 30 | 32 | 34 | 36 | 38 | 40 | 43.4 | 46.8 | 50.2 | 53.6 | 57 | 60.2 | 63.4 | 66.6 | 69.8 | 73
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 778367.4185 | 2386.5697 | -38.8849 | 2102.6619 | 4244.2086 | 6385.7554 | 8527.3021 | 10668.8489 | 12810.3957 | 9919.0071 | 7027.6184 | 4136.2298 | 67556.2787 | 94790.7679 | 122025.2571 | 149259.7464 | 176494.2356 | 203728.7248 | 230963.2141 | 267041.7275 | 303120.241 | 339198.7545 | 375277.268 | 411355.7815 | 499874.0787 | 588392.3759 | 676910.6731 | 765428.9703 | 853947.2675
Commerical(N-1) | EENS | 3229824.5729 | 9903.037 | -161.3523 | 8724.9656 | 17611.2836 | 26497.6015 | 35383.9194 | 44270.2374 | 53156.5553 | 41158.7792 | 29161.0031 | 17163.227 | 280323.821 | 393332.9481 | 506342.0753 | 619351.2024 | 732360.3295 | 845369.4566 | 958378.5837 | 1108085.8642 | 1257793.1447 | 1407500.4251 | 1557207.7056 | 1706914.9861 | 2074220.4059 | 2441525.8257 | 2808831.2456 | 3176136.6654 | 3543442.0852
Aggregate | EENS | 4008191.9914 | 12289.6066 | -200.2372 | 10827.6275 | 21855.4922 | 32883.3569 | 43911.2216 | 54939.0863 | 65966.951 | 51077.7862 | 36188.6215 | 21299.4568 | 347880.0997 | 488123.716 | 628367.3324 | 768610.9487 | 908854.5651 | 1049098.1814 | 1189341.7978 | 1375127.5917 | 1560913.3857 | 1746699.1797 | 1932484.9736 | 2118270.7676 | 2574094.4846 | 3029918.2017 | 3485741.9187 | 3941565.6357 | 4397389.3527
Residential (N-0) | EENS | 82301301.7975 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2541174.1776 | 3213547.5069 | 3761397.832 | 4511692.2864 | 6091354.1001 | 7698381.6246 | 9815681.2173 | 12144834.552 | 13742410.0241 | 15838069.3897 | 18018447.4216 | 20495702.0592 | 22817935.7015 | 25150198.2694 | 28192048.6209 | 30046176.7156 | 33926010.34 | 36254060.9991 | 39069945.1918 | 42654252.2628 | 46560504.2155 | 48074164.4673 | 52975546.4518
Commerical(N-0) | EENS | 347913427.0367 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11060494.2653 | 13984551.3583 | 15503729.4231 | 18464776.7701 | 25870861.6789 | 32977127.8831 | 43475684.5003 | 54537332.8866 | 59548583.2805 | 68187320.5186 | 78041429.9662 | 88090022.9776 | 96912100.8194 | 105686877.5705 | 117517176.1337 | 120731796.8414 | 141848513.6636 | 148836620.3788 | 159578074.544 | 173218218.8323 | 189800369.4249 | 190060866.5779 | 203166197.318
Aggregate | EENS | 430214728.8342 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 13601668.4428 | 17198098.8652 | 19265127.2551 | 22976469.0565 | 31962215.7789 | 40675509.5077 | 53291365.7176 | 66682167.4386 | 73290993.3045 | 84025389.9082 | 96059877.3877 | 108585725.0368 | 119730036.5209 | 130837075.8399 | 145709224.7546 | 150777973.557 | 175774524.0036 | 185090681.378 | 198648019.7358 | 215872471.0951 | 236360873.6404 | 238135031.0452 | 256141743.7698
Residential (N-1) | Value for Flex-1 | 788054850.6481 | 11975880.0305 | 18606592.14 | 25561354.93 | 32852226.7394 | 40491666.2924 | 48492545.1814 | 56868160.7234 | 65632249.2018 | 74798999.5036 | 84383067.1647 | 94399588.8343 | 104864197.1703 | 115793036.1801 | 127202777.0172 | 139110634.2485 | 151534382.6057 | 164492374.2344 | 178003556.4554 | 192087490.0536 | 206764368.1089 | 222055035.3856 | 237981008.2962 | 254564495.4551 | 271828418.8418 | 289796435.5882 | 308492960.4101 | 327943188.7009 | 348173120.3059
Commerical(N-1) | Value for Flex-1 | 3246496385.9232 | 49336224.763 | 76652321.9636 | 105303388.8837 | 135339101.4486 | 166810785.0237 | 199771465.8392 | 234275923.9548 | 270380747.81 | 308144390.4055 | 347627227.1634 | 388891615.5152 | 432001956.2676 | 477024756.7979 | 524028696.1321 | 573084691.96 | 624265969.6442 | 677648133.2801 | 733309238.8669 | 791329869.6496 | 851793213.6972 | 914785143.7786 | 980394299.6056 | 1048712172.509 | 1119833192.6203 | 1193854818.6294 | 1270877630.1936 | 1351005423.0743 | 1434345307.0802
Aggregate | Value for Flex-1 | 4034551236.5712 | 61312104.7935 | 95258914.1036 | 130864743.8137 | 168191328.188 | 207302451.3162 | 248264011.0206 | 291144084.6782 | 336012997.0118 | 382943389.9091 | 432010294.3281 | 483291204.3495 | 536866153.4379 | 592817792.9781 | 651231473.1493 | 712195326.2085 | 775800352.2499 | 842140507.5146 | 911312795.3223 | 983417359.7032 | 1058557581.8061 | 1136840179.1643 | 1218375307.9017 | 1303276667.9641 | 1391661611.4622 | 1483651254.2176 | 1579370590.6037 | 1678948611.7752 | 1782518427.3862
Residential (N-1) | Value for Flex-2 | 21148393.0448 | 1782193.5022 | 1836218.755 | 1891831.3995 | 1945036.4893 | 1999771.2084 | 2055973.9519 | 2114280.8795 | 2174162.4195 | 2235716.611 | 2298989.6605 | 2364209.1501 | 2431252.7456 | 2500233.9663 | 2571080.0621 | 2643640.7387 | 2718222.5242 | 2794950.7478 | 2873745.1286 | 2954074.043 | 3036623.3124 | 3121453.7491 | 3208549.0445 | 3297079.2821 | 3387947.9271 | 3481299.3297 | 3577287.7863 | 3674473.8539 | 3774283.4201
Commerical(N-1) | Value for Flex-2 | 95329595.2411 | 8033508.0235 | 8277035.0599 | 8527717.5055 | 8767547.5323 | 9014272.596 | 9267615.0027 | 9530442.3385 | 9800367.4794 | 10077832.351 | 10363045.2364 | 10657031.996 | 10959241.1904 | 11270184.5248 | 11589534.0667 | 11916612.3427 | 12252801.0738 | 12598665.2007 | 12953842.8453 | 13315937.6334 | 13688041.0091 | 14070427.0927 | 14463022.3713 | 14862085.8699 | 15271690.0949 | 15692485.7275 | 16125168.2812 | 16563249.2489 | 17013156.0349
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 116477988.2859 | 9815701.5258 | 10113253.8149 | 10419548.9051 | 10712584.0215 | 11014043.8044 | 11323588.9546 | 11644723.2179 | 11974529.8989 | 12313548.962 | 12662034.897 | 13021241.1461 | 13390493.936 | 13770418.4911 | 14160614.1287 | 14560253.0814 | 14971023.598 | 15393615.9485 | 15827587.9738 | 16270011.6764 | 16724664.3216 | 17191880.8418 | 17671571.4158 | 18159165.152 | 18659638.022 | 19173785.0573 | 19702456.0675 | 20237723.1028 | 20787439.455
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 188411324.8681 | 10726430.6318 | 11942838.0359 | 13061902.919 | 14045858.0161 | 15047134.0893 | 15966281.3827 | 16826769.1539 | 18031643.2416 | 19121727.879 | 20269467.1635 | 21725569.9002 | 23033944.1605 | 24337982.4887 | 25991759.1592 | 27339369.2398 | 28955620.0169 | 30482117.9036 | 32144536.5626 | 33677354.8608 | 35427012.9141 | 37044708.2055 | 38590971.4689 | 40462836.7672 | 42520921.9724 | 44609350.844 | 46568004.0768 | 48217070.4851 | 50357497.6749
Aggregate ($M) |  | 4773.6635 | 83805066.6002 | 122408651.5619 | 162098165.798 | 203773387.4442 | 246378772.5556 | 289199461.0223 | 336868615.0015 | 385350264.3583 | 437406213.5929 | 496940200.7891 | 558734824.3603 | 626929837.3517 | 698096485.1125 | 765303207.0742 | 838888949.3867 | 916695727.8177 | 997651064.5849 | 1080204298.1774 | 1165576929.6721 | 1257979397.1821 | 1343601440.9482 | 1452344859.7636 | 1549107622.029 | 1654064285.677 | 1766336779.4157 | 1885487666.3071 | 1989480002.0441 | 2114202497.6386
Aggregate ($M)+ Monetized Losses |  | 4774.3696 | 83854363.6002 | 122460703.1119 | 162152894.7131 | 203830895.0604 | 246439163.6023 | 289262843.7288 | 336935101.2064 | 385419969.6224 | 437479257.3152 | 497016706.3268 | 558814919.1518 | 627013653.0436 | 698184157.6908 | 765394876.9982 | 838984761.7285 | 916795832.4044 | 997755616.1461 | 1080313456.4964 | 1165690859.742 | 1258098269.3667 | 1343725431.1467 | 1452474149.5818 | 1549242398.9538 | 1654204743.2578 | 1766483117.4495 | 1885640091.0308 | 1989638726.3307 | 2114367741.201
Project Cost |  | 290
Benefit-Cost Ratio |  | 16.4609

## SCE Orange County
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| SCE Orange County | Losses (MWh) | 43573.7083 | 44329.8333 | 44869.1933 | 45408.5532 | 45947.9131 | 46487.2731 | 47026.633 | 47565.9929 | 48105.3529 | 48644.7128 | 49184.0728 | 49723.4327 | 50262.7926 | 50802.1526 | 51341.5125 | 51880.8724 | 52420.2324 | 52959.5923 | 53498.9522 | 54038.3122 | 54577.6721 | 55117.0321 | 55656.392 | 56195.7519 | 56735.1119 | 57274.4718 | 57813.8317 | 58353.1917
N-1 |  | EENS | 5 | 9.6429 | 14.2857 | 18.9286 | 23.5714 | 28.2143 | 32.8571 | 37.5 | 65.1 | 92.7 | 120.3 | 147.9 | 175.5 | 239.76 | 304.02 | 368.28 | 432.54 | 496.8 | 633.22 | 769.64 | 906.06 | 1042.48 | 1178.9 | 1398.18 | 1617.46 | 1836.74 | 2056.02 | 2275.3
N-1 |  | IP | 2.5 | 2.8571 | 3.2143 | 3.5714 | 3.9286 | 4.2857 | 4.6429 | 5 | 7.44 | 9.88 | 12.32 | 14.76 | 17.2 | 20.08 | 22.96 | 25.84 | 28.72 | 31.6 | 34.48 | 37.36 | 40.24 | 43.12 | 46 | 51.62 | 57.24 | 62.86 | 68.48 | 74.1
N-1 |  | SAIDI | 0.0091651 | 0.044606 | 0.080047 | 0.11549 | 0.15093 | 0.18637 | 0.22181 | 0.25725 | 0.72352 | 1.1898 | 1.6561 | 2.1223 | 2.5886 | 4.7002 | 6.8119 | 8.9235 | 11.0352 | 13.1468 | 20.084 | 27.0211 | 33.9583 | 40.8954 | 47.8326 | 67.486 | 87.1395 | 106.7929 | 126.4464 | 146.0998
N-1 |  | SAIFI | 0.0045825 | 0.010243 | 0.015903 | 0.021563 | 0.027223 | 0.032883 | 0.038543 | 0.044203 | 0.075363 | 0.10652 | 0.13768 | 0.16884 | 0.2 | 0.27839 | 0.35677 | 0.43515 | 0.51353 | 0.59191 | 0.74745 | 0.90299 | 1.0585 | 1.2141 | 1.3696 | 1.6214 | 1.8732 | 2.125 | 2.3768 | 2.6286
N-1 |  | PFD | 2 | 2.2857 | 2.5714 | 2.8571 | 3.1429 | 3.4286 | 3.7143 | 4 | 4.8 | 5.6 | 6.4 | 7.2 | 8 | 11.2 | 14.4 | 17.6 | 20.8 | 24 | 26.6 | 29.2 | 31.8 | 34.4 | 37 | 40.8 | 44.6 | 48.4 | 52.2 | 56
N-1 |  | Deficit Flex-1 | 993.5541 | 1506.0369 | 2018.5198 | 2531.0027 | 3043.4856 | 3555.9685 | 4068.4514 | 4580.9342 | 5093.4171 | 5605.9 | 6118.3829 | 6630.8658 | 7143.3487 | 7655.8316 | 8168.3144 | 8680.7973 | 9193.2802 | 9705.7631 | 10218.246 | 10730.7289 | 11243.2117 | 11755.6946 | 12268.1775 | 12780.6604 | 13293.1433 | 13805.6262 | 14318.1091 | 14830.5919
N-1 |  | Deficit Flex-2-1 | 56008.4017 | 58426.8449 | 60902.8323 | 62391.8256 | 63910.3881 | 65432.192 | 67096.1421 | 68769.0844 | 70464.5241 | 72182.6265 | 73960.1356 | 75757.058 | 77581.1916 | 79401.7627 | 81181.4597 | 82967.5079 | 84769.7597 | 86559.5135 | 88220.405 | 89881.2964 | 91542.1879 | 93188.7614 | 94663.5185 | 96123.9576 | 97584.3966 | 99059.1537 | 100304.8223 | 101550.4909
N-1 |  | Deficit Flex-2-2 | 10473.003 | 12327.6186 | 14391.879 | 15686.4316 | 17094.0777 | 18566.6433 | 20254.0187 | 22013.3705 | 23859.8697 | 25779.4827 | 27842.3594 | 30005.4071 | 32255.8746 | 34569.9898 | 36885.3193 | 39294.771 | 41792.6974 | 44365.0533 | 46822.5519 | 49360.7464 | 51939.8619 | 54588.093 | 57026.817 | 59516.8469 | 62078.2248 | 64756.0181 | 67061.3032 | 69421.6627
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.64 | 73.28 | 109.92 | 146.56 | 183.2 | 253.84 | 324.48 | 395.12 | 465.76 | 536.4 | 714.24 | 892.08 | 1069.92 | 1247.76 | 1425.6
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.92 | 21.84 | 32.76 | 43.68 | 54.6 | 65.92 | 77.24 | 88.56 | 99.88 | 111.2 | 120.68 | 130.16 | 139.64 | 149.12 | 158.6
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20254 | 0.40508 | 0.60762 | 0.81016 | 1.0127 | 2.1148 | 3.2169 | 4.319 | 5.4212 | 6.5233 | 13.7295 | 20.9358 | 28.142 | 35.3482 | 42.5545
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040508 | 0.081016 | 0.12152 | 0.16203 | 0.20254 | 0.28064 | 0.35873 | 0.43683 | 0.51493 | 0.59302 | 0.78964 | 0.98625 | 1.1829 | 1.3795 | 1.5761
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6.2 | 7.4 | 8.6 | 9.8 | 11 | 14.2 | 17.4 | 20.6 | 23.8 | 27
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108080.5699 | 374145.0391 | 747332.649 | 1252882.7096 | 1799896.6551 | 2099502.2836 | 2814778.4968 | 3398799.516 | 4342375.6756 | 4821378.348 | 5850472.8919 | 7066227.7113 | 8483569.782 | 9954915.2655 | 11476252.3466
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609029.1041 | 2109560.092 | 3953519.5525 | 6679805.5678 | 9458028.0234 | 10015314.4369 | 13656644.3692 | 15801138.5005 | 20354736.2592 | 21344938.9124 | 25766135.0707 | 31037346.988 | 36784087.4023 | 42906446.2459 | 49882217.5523
N-1 Monetized | Residential | $ | 660.9588 | 1399.6941 | 2138.4294 | 2877.1647 | 3615.9 | 4354.6353 | 5093.3706 | 5832.1059 | 11039.3498 | 16246.5937 | 21453.8377 | 26661.0816 | 31868.3255 | 47066.1112 | 62263.8969 | 77461.6826 | 92659.4683 | 107857.254 | 146801.2119 | 185745.1697 | 224689.1276 | 263633.0855 | 302577.0433 | 383351.8441 | 464126.6448 | 544901.4455 | 625676.2463 | 706451.047
N-1 Monetized | Commercial | $ | 2742.6391 | 5808.0108 | 8873.3824 | 11938.7541 | 15004.1258 | 18069.4974 | 21134.8691 | 24200.2407 | 45807.6256 | 67415.0105 | 89022.3954 | 110629.7803 | 132237.1652 | 195300.1616 | 258363.158 | 321426.1543 | 384489.1507 | 447552.1471 | 609149.5484 | 770746.9497 | 932344.3509 | 1093941.7522 | 1255539.1535 | 1590713.0445 | 1925886.9354 | 2261060.8264 | 2596234.7174 | 2931408.6084
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 3198990.7073 | 3871218.4666 | 4557419.954 | 5046322.0111 | 5613392.7018 | 6269805.0456 | 6956187.997 | 7743781.1049 | 8477502.7487 | 9407600.3959 | 10247859.3068 | 11253998.3465 | 12368529.0622 | 13532588.3732 | 14655219.7822 | 15964764.1984 | 17339527.5774 | 18768603.217 | 20226314.7327 | 21764134.0648 | 23296596.0078 | 24945796.6189 | 26717318.6534 | 28524096.3821 | 30417221.4181 | 32491727.0406 | 34433544.1314 | 36442341.9842
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 64717.6233 | Losses (MWh) | 6508.0417 | 6558.2167 | 6615.3606 | 6672.5045 | 6729.6484 | 6786.7923 | 6843.9362 | 6901.0801 | 6958.224 | 7015.3679 | 7072.5119 | 7129.6558 | 7186.7997 | 7243.9436 | 7301.0875 | 7358.2314 | 7415.3753 | 7472.5192 | 7529.6631 | 7586.8071 | 7643.951 | 7701.0949 | 7758.2388 | 7815.3827 | 7872.5266 | 7929.6705 | 7986.8144 | 8043.9583
| 3228185.9265 | Losses ($) | 260321.6667 | 268886.8833 | 278010.5282 | 287422.3011 | 297130.906 | 307145.3022 | 317474.7115 | 328128.6253 | 339116.8132 | 350449.3301 | 362136.5248 | 374189.0484 | 386617.8628 | 399434.2499 | 412649.8201 | 426276.5224 | 440326.6537 | 454812.8687 | 469748.1904 | 485146.02 | 501020.1486 | 517384.7673 | 534254.4793 | 551644.3115 | 569569.7262 | 588046.634 | 607091.406 | 626720.8876
N-1 | 7597.9801 | EENS | 13 | 30.3571 | 57.5476 | 84.7381 | 111.9286 | 139.119 | 166.3095 | 193.5 | 283 | 372.5 | 462 | 551.5 | 813.15 | 1038.14 | 1263.13 | 1488.12 | 1713.11 | 1938.1 | 2481.75 | 3025.4 | 3569.05 | 4112.7 | 4083.8 | 4659.1 | 5234.4 | 5809.7 | 6385 | 6960.3
N-1 | 144.9144 | IP | 1 | 3.1429 | 5.669 | 8.1952 | 10.7214 | 13.2476 | 15.7738 | 18.3 | 18.81 | 19.32 | 19.83 | 20.34 | 22.3 | 23.82 | 25.34 | 26.86 | 28.38 | 29.9 | 29 | 28.1 | 27.2 | 26.3 | 25.4 | 31.18 | 36.96 | 42.74 | 48.52 | 54.3
N-1 | 1059.0133 | SAIDI | 0.19423 | 0.41144 | 1.0523 | 1.6933 | 2.3342 | 2.9751 | 3.616 | 4.2569 | 9.0299 | 13.803 | 18.576 | 23.349 | 51.5482 | 78.102 | 104.6558 | 131.2096 | 157.7634 | 184.3172 | 285.5151 | 386.7131 | 487.9111 | 589.109 | 690.307 | 909.8708 | 1129.4347 | 1348.9986 | 1568.5624 | 1788.1263
N-1 | 6.1176 | SAIFI | 0.0094232 | 0.020681 | 0.041688 | 0.062696 | 0.083704 | 0.10471 | 0.12572 | 0.14673 | 0.22051 | 0.2943 | 0.36808 | 0.44186 | 0.67239 | 0.8557 | 1.039 | 1.2223 | 1.4056 | 1.5889 | 1.9532 | 2.3175 | 2.6818 | 3.0461 | 3.4104 | 3.8922 | 4.374 | 4.8557 | 5.3375 | 5.8193
N-1 | 617.1566 | PFD | 16 | 25.7143 | 30.7619 | 35.8095 | 40.8571 | 45.9048 | 50.9524 | 56 | 62.2 | 68.4 | 74.6 | 80.8 | 89.8333 | 96.4667 | 103.1 | 109.7333 | 116.3667 | 123 | 131.8 | 140.6 | 149.4 | 158.2 | 167 | 174.6 | 182.2 | 189.8 | 197.4 | 205
N-1 | 252249.9385 | Flex-1 | 5333.4799 | 8084.5302 | 10835.5805 | 13586.6308 | 16337.6811 | 19088.7313 | 21839.7816 | 24590.8319 | 27341.8822 | 30092.9325 | 32843.9828 | 35595.0331 | 38346.0834 | 41097.1336 | 43848.1839 | 46599.2342 | 49350.2845 | 52101.3348 | 54852.3851 | 57603.4354 | 60354.4857 | 63105.5359 | 65856.5862 | 68607.6365 | 71358.6868 | 74109.7371 | 76860.7874 | 79611.8377
N-1 | 1329505.5441 | Flex-2-1 | 138604.1342 | 139542.8424 | 140424.0064 | 140928.8544 | 141421.1745 | 141893.2118 | 142393.5166 | 142867.788 | 143319.5619 | 143748.6732 | 144169.5018 | 144570.9171 | 144962.1626 | 145339.9293 | 145690.4046 | 146034.5286 | 146379.4904 | 146719.9089 | 147035.8172 | 147351.7256 | 147667.6339 | 147980.8189 | 148261.3238 | 148539.1052 | 148816.8867 | 149097.3915 | 149334.3228 | 149571.2541
N-1 | 735410.3655 | Flex-2-2 | 50540.9619 | 55182.6613 | 59985.6957 | 62931.7944 | 65894.9038 | 68822.76 | 72067.297 | 75347.1577 | 78698.4846 | 82123.5164 | 85667.9229 | 89210.1375 | 92847.4439 | 96491.6634 | 100042.0588 | 103633.6982 | 107303.5324 | 110990.8302 | 114465.1688 | 117969.8049 | 121545.5696 | 125149.4725 | 128371.1146 | 131544.0426 | 134727.0103 | 137930.6128 | 140665.5358 | 143401.0656
N-0 | 20371.8447 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3386.4267 | 3929.17 | 4471.9133 | 5014.6567 | 5557.4 | 6316.16 | 7074.92 | 7833.68 | 8592.44 | 9351.2 | 10100.32 | 10849.44 | 11598.56 | 12347.68 | 13096.8
N-0 | 1184.7372 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 209.08 | 213.16 | 217.24 | 221.32 | 225.4 | 227.76 | 230.12 | 232.48 | 234.84 | 237.2 | 240.16 | 243.12 | 246.08 | 249.04 | 252
N-0 | 1742.0508 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.7592 | 254.9558 | 310.1524 | 365.349 | 420.5456 | 549.8023 | 679.059 | 808.3157 | 937.5725 | 1066.8292 | 1283.8953 | 1500.9615 | 1718.0277 | 1935.0938 | 2152.16
N-0 | 21.6476 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6026 | 4.1787 | 4.7548 | 5.3309 | 5.907 | 6.7116 | 7.5162 | 8.3208 | 9.1254 | 9.93 | 10.72 | 11.5099 | 12.2998 | 13.0897 | 13.8796
N-0 | 267.1157 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 46.6667 | 51 | 55.3333 | 59.6667 | 64 | 69.4 | 74.8 | 80.2 | 85.6 | 91 | 95.8 | 100.6 | 105.4 | 110.2 | 115
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 4146212.9366 | 2003.2136 | 5296.9624 | 13157.7126 | 21018.4627 | 28879.2129 | 36739.963 | 44600.7132 | 52461.4633 | 94815.5736 | 137169.6839 | 179523.7941 | 221877.9044 | 360669.3299 | 489470.2138 | 618271.0976 | 747071.9814 | 875872.8652 | 1004673.7491 | 1310151.2848 | 1615628.8206 | 1921106.3564 | 2226583.8921 | 2532061.4279 | 3005188.426 | 3478315.4241 | 3951442.4221 | 4424569.4202 | 4897696.4183
Commerical(N-1) | EENS | 17204651.8241 | 8312.3063 | 21979.6704 | 54597.7418 | 87215.8132 | 119833.8846 | 152451.956 | 185070.0274 | 217688.0987 | 393435.879 | 569183.6593 | 744931.4396 | 920679.2199 | 1496592.2736 | 2031049.7157 | 2565507.1579 | 3099964.6001 | 3634422.0422 | 4168879.4844 | 5436454.1901 | 6704028.8959 | 7971603.6016 | 9239178.3073 | 10506753.013 | 12469986.7869 | 14433220.5607 | 16396454.3345 | 18359688.1084 | 20322921.8822
Aggregate | EENS | 21350864.7607 | 10315.5198 | 27276.6329 | 67755.4544 | 108234.2759 | 148713.0975 | 189191.919 | 229670.7405 | 270149.5621 | 488251.4526 | 706353.3432 | 924455.2337 | 1142557.1243 | 1857261.6035 | 2520519.9295 | 3183778.2555 | 3847036.5815 | 4510294.9075 | 5173553.2335 | 6746605.475 | 8319657.7164 | 9892709.9579 | 11465762.1994 | 13038814.4409 | 15475175.2129 | 17911535.9848 | 20347896.7567 | 22784257.5286 | 25220618.3005
Residential (N-0) | EENS | 115744145.6004 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17758386.3868 | 20622652.747 | 23950766.3392 | 27587434.632 | 31741320.6982 | 36371571.8443 | 41723317.0004 | 46666347.9384 | 51685235.5429 | 57131638.5789 | 62341603.6008 | 68687348.3435 | 75589326.9932 | 80341239.4697 | 88465069.5789
Commerical(N-0) | EENS | 494155901.4942 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 77066166.0066 | 88282983.4741 | 102741449.2033 | 117665560.5431 | 134254403.4886 | 154543031.9925 | 177075859.0006 | 195935357.2557 | 217286134.0317 | 239679344.52 | 259644693.6145 | 285351965.3639 | 314742732.0651 | 329129734.1207 | 355270768.0098
Aggregate | EENS | 609900047.0946 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 94824552.3934 | 108905636.2211 | 126692215.5425 | 145252995.1751 | 165995724.1868 | 190914603.8368 | 218799176.001 | 242601705.1941 | 268971369.5746 | 296810983.099 | 321986297.2153 | 354039313.7074 | 390332059.0583 | 409470973.5905 | 443735837.5886
Residential (N-1) | Value for Flex-1 | 1384736347.2038 | 21042495.8115 | 32693787.7405 | 44914492.7061 | 57725799.3026 | 71149599.671 | 85208511.4332 | 99925900.2838 | 115325903.2573 | 131433452.6917 | 148274300.9083 | 165875045.6279 | 184263156.1453 | 203467000.2851 | 223515872.1593 | 244440020.752 | 266270679.3543 | 289040095.8737 | 312781564.0445 | 337529455.5639 | 363319253.1817 | 390187584.7707 | 418172258.4059 | 447312298.4824 | 477647982.9012 | 509220881.3544 | 542073894.741 | 576251295.746 | 611798770.6171
Commerical(N-1) | Value for Flex-1 | 5704604879.9228 | 86687349.9309 | 134686390.9974 | 185031204.5234 | 237809079.7313 | 293110204.1968 | 351027754.2108 | 411657987.8479 | 475100340.8204 | 541457525.1991 | 610835631.0838 | 683344231.3094 | 759096489.2769 | 838209269.9982 | 920803254.4498 | 1007003057.3301 | 1096937348.3205 | 1190738976.9496 | 1288545101.1674 | 1390497319.7356 | 1496741808.5439 | 1607429460.9677 | 1722716032.3825 | 1842762288.9548 | 1967734160.8356 | 2097802899.8798 | 2233145242.0256 | 2373943574.4664 | 2520386107.7529
Aggregate | Value for Flex-1 | 7089341227.1267 | 107729845.7425 | 167380178.7379 | 229945697.2295 | 295534879.0339 | 364259803.8678 | 436236265.6441 | 511583888.1317 | 590426244.0776 | 672890977.8908 | 759109931.9921 | 849219276.9373 | 943359645.4222 | 1041676270.2833 | 1144319126.6091 | 1251443078.0822 | 1363208027.6748 | 1479779072.8233 | 1601326665.2119 | 1728026775.2994 | 1860061061.7256 | 1997617045.7384 | 2140888290.7884 | 2290074587.4373 | 2445382143.7368 | 2607023781.2342 | 2775219136.7666 | 2950194870.2124 | 3132184878.37
Residential (N-1) | Value for Flex-2 | 54839473.0902 | 4614910.5165 | 4762319.5242 | 4912201.6956 | 5053108.4359 | 5197529.9599 | 5345250.297 | 5498199.6814 | 5654425.3998 | 5814113.3603 | 5977309.3577 | 6144678.315 | 6315831.7996 | 6491247.1415 | 6670867.1978 | 6854127.2818 | 7042074.8044 | 7235177.2873 | 7433303.4168 | 7635541.0608 | 7843244.7724 | 8056561.4563 | 8275489.6495 | 8498455.6481 | 8727237.7586 | 8962147.4398 | 9203516.1889 | 9448595.0718 | 9700175.7012
Commerical(N-1) | Value for Flex-2 | 247197258.0535 | 20802410.4093 | 21466878.9107 | 22142495.5738 | 22777654.1169 | 23428656.082 | 24094527.9481 | 24783970.5395 | 25488181.7043 | 26207999.4516 | 26943630.2084 | 27698071.2157 | 28469571.5551 | 29260282.8641 | 30069947.5616 | 30896020.2374 | 31743222.255 | 32613661.0394 | 33506744.6746 | 34418361.5858 | 35354617.6271 | 36316174.9944 | 37303027.0922 | 38308080.2117 | 39339350.339 | 40398241.4227 | 41486247.7362 | 42590978.0416 | 43725015.9575
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 302036731.1437 | 25417320.9258 | 26229198.4349 | 27054697.2694 | 27830762.5528 | 28626186.0419 | 29439778.2452 | 30282170.2209 | 31142607.104 | 32022112.8118 | 32920939.5661 | 33842749.5307 | 34785403.3547 | 35751530.0056 | 36740814.7594 | 37750147.5191 | 38785297.0594 | 39848838.3267 | 40940048.0915 | 42053902.6466 | 43197862.3995 | 44372736.4508 | 45578516.7417 | 46806535.8598 | 48066588.0976 | 49360388.8625 | 50689763.9251 | 52039573.1134 | 53425191.6587
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 239375699.0796 | 13326788.2405 | 14821135.2007 | 16416018.9731 | 17597309.9813 | 18879048.163 | 20042784.3583 | 21242044.641 | 22646153.492 | 24191373.6887 | 25623487.1658 | 27581559.9305 | 29206384.9534 | 30959754.1019 | 32862372.5369 | 34793137.4101 | 36872350.062 | 38982831.2622 | 41233672.3931 | 43425280.2116 | 45764429.5336 | 48098952.1912 | 50435617.494 | 52949971.441 | 55508681.2434 | 57982016.7188 | 60614183.5375 | 62944321.862 | 65700080.3876
Aggregate ($M) |  | 8262.0046 | 148422810.4711 | 213551634.8511 | 281225311.4592 | 351872947.5703 | 424896011.1591 | 500539731.3149 | 582866464.7568 | 668632858.6167 | 759947769.2475 | 858706084.8656 | 964514644.7028 | 1076834813.9692 | 1194229224.0216 | 1311267386.2282 | 1436075777.4879 | 1569404926.9202 | 1708374032.4948 | 1854669663.1168 | 2011167167.4694 | 2176142187.3761 | 2342583149.5325 | 2517339556.7981 | 2699680892.2779 | 2886418885.506 | 3086317036.5076 | 3297203040.0442 | 3497433996.3069 | 3720266606.3054
Aggregate ($M)+ Monetized Losses |  | 8265.2328 | 148683132.1378 | 213820521.7345 | 281503321.9874 | 352160369.8714 | 425193142.0651 | 500846876.6171 | 583183939.4683 | 668960987.2421 | 760286886.0607 | 859056534.1956 | 964876781.2276 | 1077209003.0176 | 1194615841.8844 | 1311666820.4781 | 1436488427.308 | 1569831203.4426 | 1708814359.1485 | 1855124475.9856 | 2011636915.6598 | 2176627333.3961 | 2343084169.6811 | 2517856941.5654 | 2700215146.7572 | 2886970529.8175 | 3086886606.2337 | 3297791086.6782 | 3498041087.7129 | 3720893327.193
Project Cost |  | 806
Benefit-Cost Ratio |  | 10.2546

## VS to VN & Central BESS VS VN
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Energy Storage at Pechanga and Allesando + Ties between VN+VS | Losses (MWh) | 49722.95 | 50479.4 | 51032.9519 | 51586.5038 | 52140.0558 | 52693.6077 | 53247.1596 | 53800.7115 | 54354.2635 | 54907.8154 | 55461.3673 | 56014.9192 | 56568.4712 | 57122.0231 | 57675.575 | 58219.1635 | 58762.7519 | 59306.3404 | 59849.9288 | 60393.5173 | 60937.1058 | 61480.6942 | 62024.2827 | 62567.8712 | 63111.4596 | 63655.0481 | 64198.6365 | 64742.225
N-1 |  | EENS | 11.6 | 34.8 | 65.5667 | 96.3333 | 127.1 | 157.8667 | 188.6333 | 219.4 | 321.975 | 424.55 | 527.125 | 629.7 | 778.9 | 961.5167 | 1144.1333 | 1326.75 | 1509.3667 | 1725.4 | 1997.16 | 2268.92 | 2540.68 | 2812.44 | 3084.2 | 3399.8 | 3715.4 | 4031 | 4346.6 | 4662.2
N-1 |  | IP | 5.7 | 11.1 | 13.9667 | 16.8333 | 19.7 | 22.5667 | 25.4333 | 28.3 | 30.75 | 33.2 | 35.65 | 38.1 | 42.1 | 49 | 55.9 | 62.8 | 69.7 | 79.5 | 79.08 | 78.66 | 78.24 | 77.82 | 77.4 | 90.9 | 104.4 | 117.9 | 131.4 | 144.9
N-1 |  | SAIDI | 0.042384 | 0.15894 | 0.88764 | 1.6163 | 2.345 | 3.0737 | 3.8024 | 4.5311 | 8.8152 | 13.0992 | 17.3833 | 21.6674 | 29.5008 | 46.6295 | 63.7583 | 80.887 | 98.0157 | 124.4397 | 164.5971 | 204.7544 | 244.9118 | 285.0692 | 325.2266 | 389.7102 | 454.1938 | 518.6774 | 583.161 | 647.6446
N-1 |  | SAIFI | 0.010596 | 0.031788 | 0.059915 | 0.088042 | 0.11617 | 0.1443 | 0.17242 | 0.20055 | 0.29596 | 0.39137 | 0.48678 | 0.58219 | 0.72138 | 0.892 | 1.0626 | 1.2333 | 1.4039 | 1.6059 | 1.8633 | 2.1206 | 2.3779 | 2.6352 | 2.8926 | 3.192 | 3.4914 | 3.7909 | 4.0903 | 4.3897
N-1 |  | PFD | 4 | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 27 | 31 | 35 | 39 | 44 | 51 | 58 | 65 | 72 | 81 | 87.6 | 94.2 | 100.8 | 107.4 | 114 | 121.4 | 128.8 | 136.2 | 143.6 | 151
N-1 |  | Deficit Flex-1 | 4238.9824 | 6425.4824 | 8611.9824 | 10798.4824 | 12984.9824 | 15171.4824 | 17357.9824 | 19544.4824 | 21730.9824 | 23917.4824 | 26103.9824 | 28290.4824 | 30476.9824 | 32663.4824 | 34849.9824 | 35619.2872 | 36388.5921 | 37157.8969 | 37927.2017 | 38696.5065 | 39465.8113 | 40235.1161 | 41004.4209 | 41773.7257 | 42543.0305 | 43312.3353 | 44081.6401 | 44850.9449
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 17164.3208 | 19844.0887 | 22754.5274 | 24601.2435 | 26524.5104 | 28541.0948 | 30814.4348 | 33148.2171 | 35561.9498 | 38077.7187 | 40736.7643 | 43501.2116 | 46385.9444 | 49358.9359 | 52298.7216 | 55356.3439 | 58553.2882 | 61842.499 | 65024.8853 | 68293.2688 | 71656.491 | 75060.9515 | 78184.8129 | 81331.7015 | 84513.9878 | 87765.4351 | 90580.7698 | 93440.6833
|  | EENS(Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS(Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 2477.0702 | 10015.3244 | 17553.5786 | 25091.8328 | 32630.087 | 40168.3412 | 47706.5954 | 55244.8497 | 50980.8962 | 46716.9428 | 42452.9894 | 38189.0359 | 257888.2831 | 367581.3421 | 477274.4011 | 586967.4601 | 696660.5191 | 696347.3899 | 871852.4632 | 1047357.5364 | 1222862.6096 | 1398367.6829 | 1573872.7561 | 1825117.7823 | 2076362.8084 | 2327607.8345 | 2578852.8607 | 2830097.8868
N-1 Monetized | Commercial | $ | 10278.5676 | 41558.4466 | 72838.3256 | 104118.2047 | 135398.0837 | 166677.9627 | 197957.8418 | 229237.7208 | 211544.5064 | 193851.2921 | 176158.0778 | 158464.8634 | 1070103.776 | 1525273.5699 | 1980443.3637 | 2435613.1576 | 2890782.9514 | 2889483.6265 | 3617739.4408 | 4345995.2551 | 5074251.0694 | 5802506.8837 | 6530762.6981 | 7573300.3736 | 8615838.0492 | 9658375.7247 | 10700913.4003 | 11743451.0759
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5110374.2214 | 6015097.5811 | 6967510.5921 | 7745187.9968 | 8491036.7137 | 9233048.7464 | 10172667.8173 | 11216525.0586 | 12260160.0595 | 13330830.0069 | 14604368.7155 | 15898045.9904 | 17328004.7347 | 18766389.6983 | 20232001.0865 | 21817429.4974 | 23600568.0435 | 25503802.0729 | 27434997.0562 | 29443388.6443 | 31566313.1487 | 33843442.2534 | 36000441.2918 | 38358137.1162 | 40806428.0067 | 43292848.4471 | 45372446.2399 | 47951699.3087
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 6657.0645 | Losses (MWh) | 358.8 | 408.65 | 451.6019 | 494.5538 | 537.5058 | 580.4577 | 623.4096 | 666.3615 | 709.3135 | 752.2654 | 795.2173 | 838.1692 | 881.1212 | 924.0731 | 967.025 | 1019.9404 | 1072.8558 | 1125.7712 | 1178.6865 | 1231.6019 | 1284.5173 | 1337.4327 | 1390.3481 | 1443.2635 | 1496.1788 | 1549.0942 | 1602.0096 | 1654.925
| 355383.2586 | Losses ($) | 14352 | 16754.65 | 18978.5708 | 21303.216 | 23732.2319 | 26269.384 | 28918.5611 | 31683.7787 | 34569.1831 | 37579.0553 | 40717.8154 | 43990.0266 | 47400.3997 | 50953.7977 | 54655.2404 | 59087.1116 | 63706.4168 | 68519.7578 | 73533.9494 | 78756.0257 | 84193.2471 | 89853.1071 | 95743.3393 | 101871.9249 | 108247.1002 | 114877.3643 | 121771.4871 | 128938.5178
N-1 | 3417.8021 | EENS | 6.4 | 5.2 | 6.2667 | 7.3333 | 8.4 | 9.4667 | 10.5333 | 11.6 | 26.125 | 40.65 | 55.175 | 69.7 | 209.75 | 316.3833 | 423.0167 | 529.65 | 636.2833 | 709.5 | 1117.81 | 1526.12 | 1934.43 | 2342.74 | 2178.5 | 2657.48 | 3136.46 | 3615.44 | 4094.42 | 4573.4
N-1 | -54.568 | IP | -2.2 | -5.1 | -5.0833 | -5.0667 | -5.05 | -5.0333 | -5.0167 | -5 | -4.5 | -4 | -3.5 | -3 | -2.6 | -5.1 | -7.6 | -10.1 | -12.6 | -18 | -15.6 | -13.2 | -10.8 | -8.4 | -6 | -8.1 | -10.2 | -12.3 | -14.4 | -16.5
N-1 | 635.0181 | SAIDI | 0.16101 | 0.2971 | 0.24476 | 0.19242 | 0.14007 | 0.087731 | 0.035388 | -0.016954 | 0.93827 | 1.8935 | 2.8487 | 3.804 | 24.636 | 36.1727 | 47.7094 | 59.2461 | 70.7829 | 73.0243 | 141.0021 | 208.9798 | 276.9575 | 344.9353 | 412.913 | 587.6467 | 762.3804 | 937.1141 | 1111.8478 | 1286.5815
N-1 | 2.697 | SAIFI | 0.0034097 | -0.00086517 | -0.0023245 | -0.0037839 | -0.0052433 | -0.0067026 | -0.008162 | -0.0096214 | -8.535e-05 | 0.0094507 | 0.018987 | 0.028523 | 0.15102 | 0.24208 | 0.33314 | 0.4242 | 0.51527 | 0.57489 | 0.8374 | 1.0999 | 1.3624 | 1.6249 | 1.8874 | 2.3216 | 2.7557 | 3.1899 | 3.6241 | 4.0583
N-1 | 387.0171 | PFD | 14 | 23 | 25.3333 | 27.6667 | 30 | 32.3333 | 34.6667 | 37 | 40 | 43 | 46 | 49 | 53.8333 | 56.6667 | 59.5 | 62.3333 | 65.1667 | 66 | 70.8 | 75.6 | 80.4 | 85.2 | 90 | 94 | 98 | 102 | 106 | 110
N-1 | 112489.2183 | Flex-1 | 2088.0515 | 3165.0847 | 4242.1179 | 5319.151 | 6396.1842 | 7473.2174 | 8550.2506 | 9627.2837 | 10704.3169 | 11781.3501 | 12858.3832 | 13935.4164 | 15012.4496 | 16089.4828 | 17166.5159 | 19660.7443 | 22154.9727 | 24649.201 | 27143.4294 | 29637.6578 | 32131.8861 | 34626.1145 | 37120.3429 | 39614.5713 | 42108.7996 | 44603.028 | 47097.2564 | 49591.4847
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 625479.561 | Flex-2-2 | 43849.6441 | 47666.1912 | 51623.0473 | 54016.9826 | 56464.4711 | 58848.3085 | 61506.8809 | 64212.3112 | 66996.4044 | 69825.2804 | 72773.518 | 75714.333 | 78717.3741 | 81702.7173 | 84628.6566 | 87572.1253 | 90542.9416 | 93513.3844 | 96262.8354 | 99037.2825 | 101828.9405 | 104676.614 | 107213.1187 | 109729.1881 | 112291.2474 | 114921.1958 | 117146.0692 | 119382.045
N-0 | 21183.8076 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 | 1335.7024 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 | 1756.8124 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 | 22.5453 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 | 284.3733 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 1998483.6243 | 187.1022 | -3318.6679 | -2257.4366 | -1196.2054 | -134.9742 | 926.2571 | 1987.4883 | 3048.7196 | 54874.0272 | 106699.3348 | 158524.6424 | 210349.95 | 134649.3724 | 168954.9829 | 203260.5935 | 237566.204 | 271871.8145 | 416183.6132 | 585100.0335 | 754016.4539 | 922932.8743 | 1091849.2947 | 1260765.7151 | 1563422.4878 | 1866079.2605 | 2168736.0331 | 2471392.8058 | 2774049.5785
Commerical(N-1) | EENS | 8292679.4782 | 776.3778 | -13770.7654 | -9367.2014 | -4963.6373 | -560.0733 | 3843.4907 | 8247.0547 | 12650.6187 | 227698.9982 | 442747.3777 | 657795.7573 | 872844.1368 | 558725.6627 | 701076.3074 | 843426.9521 | 985777.5968 | 1128128.2415 | 1726948.005 | 2427864.2977 | 3128780.5904 | 3829696.8831 | 4530613.1758 | 5231529.4685 | 6487399.4577 | 7743269.447 | 8999139.4362 | 10255009.4255 | 11510879.4147
Aggregate | EENS | 10291163.1025 | 963.48 | -17089.4332 | -11624.638 | -6159.8427 | -695.0475 | 4769.7478 | 10234.543 | 15699.3383 | 282573.0254 | 549446.7126 | 816320.3997 | 1083194.0868 | 693375.0352 | 870031.2904 | 1046687.5456 | 1223343.8008 | 1400000.056 | 2143131.6182 | 3012964.3313 | 3882797.0443 | 4752629.7574 | 5622462.4705 | 6492295.1836 | 8050821.9455 | 9609348.7074 | 11167875.4694 | 12726402.2313 | 14284928.9932
Residential (N-0) | EENS | 122402385.4505 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17866466.9567 | 20996797.7861 | 24698098.9882 | 28840317.3417 | 33541217.3533 | 38471074.1279 | 44538095.4972 | 50065147.4545 | 56027611.2185 | 61953016.927 | 68192076.4928 | 75753576.0548 | 84072896.7752 | 90296154.7352 | 99941321.9255
Commerical(N-0) | EENS | 524690134.185 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 77675195.1106 | 90392543.5661 | 106694968.7558 | 124345366.1109 | 143712431.512 | 164558346.4294 | 190732503.3698 | 211736495.7562 | 237640870.2909 | 261024283.4324 | 285410828.6852 | 316389312.3519 | 351526819.4674 | 372036180.3666 | 405152985.562
Aggregate | EENS | 647092519.6355 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 95541662.0673 | 111389341.3522 | 131393067.744 | 153185683.4525 | 177253648.8653 | 203029420.5574 | 235270598.867 | 261801643.2106 | 293668481.5094 | 322977300.3594 | 353602905.1779 | 392142888.4066 | 435599716.2426 | 462332335.1019 | 505094307.4875
Residential (N-1) | Value for Flex-1 | 635671269.5836 | 8238114.0347 | 12799582.0479 | 17583974.6405 | 22599587.1239 | 27854990.2474 | 33359038.7851 | 39120880.3807 | 45149964.6569 | 51456052.5967 | 58049226.2056 | 64939898.462 | 72138823.5649 | 79657107.4864 | 87506218.8392 | 95698000.0675 | 112342613.0852 | 129759645.5037 | 147977315.41 | 167024769.0332 | 186932109.5153 | 207730426.541 | 229451826.8495 | 252129465.6568 | 275797579.0127 | 300491517.1204 | 326247778.6465 | 353104046.0508 | 381099221.9637
Commerical(N-1) | Value for Flex-1 | 2618732030.6971 | 33938002.4352 | 52729574.3762 | 72439513.6626 | 93101993.9295 | 114752323.5136 | 137426980.8307 | 161163650.8115 | 186001262.4283 | 211980027.3442 | 239141479.7169 | 267528517.1911 | 297185443.1142 | 328158010.0103 | 360493464.3491 | 394240592.6487 | 462810281.6273 | 534562054.6845 | 609612159.9685 | 688080669.2325 | 770091596.3597 | 855773019.425 | 945257206.3959 | 1038680744.5782 | 1136184673.9155 | 1237914624.2544 | 1344020956.6891 | 1454658909.1053 | 1569988746.0444
Aggregate | Value for Flex-1 | 3254403300.2807 | 42176116.4699 | 65529156.424 | 90023488.3031 | 115701581.0534 | 142607313.761 | 170786019.6158 | 200284531.1923 | 231151227.0853 | 263436079.941 | 297190705.9225 | 332468415.6531 | 369324266.6791 | 407815117.4966 | 447999683.1883 | 489938592.7162 | 575152894.7125 | 664321700.1882 | 757589475.3784 | 855105438.2656 | 957023705.875 | 1063503445.966 | 1174709033.2454 | 1290810210.235 | 1411982252.9283 | 1538406141.3748 | 1670268735.3356 | 1807762955.1561 | 1951087968.008
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 201421523.7425 | 11415404.7265 | 12677256.0862 | 14005928.335 | 14898443.9956 | 16001404.1511 | 17079540.6575 | 18025564.8207 | 19173409.5383 | 20408716.3778 | 21700257.5548 | 23225050.5217 | 24562337.3095 | 26000278.4294 | 27628571.2119 | 29216356.1057 | 31019684.7629 | 32721790.7961 | 34498473.5373 | 36216597.8881 | 38085174.9541 | 39829235.0504 | 41537971.8595 | 43666848.8026 | 45674640.5094 | 47592810.1302 | 49813062.131 | 52005419.7536 | 54190723.0631
Aggregate ($M) |  | 4113.2085 | 55531024.7188 | 83283168.9217 | 111758934.5329 | 141395626.9326 | 171590282.8534 | 202502041.1694 | 237849021.5787 | 274488040.3429 | 314482422.7478 | 359785782.9883 | 409456389.6453 | 463310621.1901 | 518493178.9885 | 572039947.7579 | 631590977.7197 | 738788991.0202 | 851629174.4929 | 971484729.3992 | 1097364421.0424 | 1234262276.7405 | 1369886953.9845 | 1515537949.0848 | 1663946654.5806 | 1819310620.5611 | 1987751188.6191 | 2166849389.1786 | 2334827112.2428 | 2524657927.5518
Aggregate ($M)+ Monetized Losses |  | 4113.5639 | 55545376.7188 | 83299923.5717 | 111777913.1037 | 141416930.1487 | 171614015.0853 | 202528310.5534 | 237877940.1398 | 274519724.1216 | 314516991.9309 | 359823362.0436 | 409497107.4606 | 463354611.2167 | 518540579.3882 | 572090901.5556 | 631645632.96 | 738848078.1318 | 851692880.9097 | 971553249.157 | 1097437954.9918 | 1234341032.7662 | 1369971147.2316 | 1515627802.1919 | 1664042397.9199 | 1819412492.486 | 1987859435.7192 | 2166964266.5429 | 2334948883.73 | 2524786866.0697
Project Cost |  | 726
Benefit-Cost Ratio |  | 5.6661
Market Participation Revenue (All costs are $x1,000) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5358.25 | 7225.9345 | 9093.6191 | 10961.3036 | 12828.9881 | 14696.6727 | 16564.3572 | 18017.4731 | 19470.5889 | 20923.7048 | 22376.8207 | 23829.9366 | 24219.2132 | 24608.4897 | 24997.7663 | 25387.0429 | 25776.3195 | 25968.5583 | 26160.7971 | 26353.0359

## VS to VN to VST & Cen BESS VS
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Valley South to Valley North to Vista and Centralized BESS in Valley South | Losses (MWh) | 49722.95 | 50479.4 | 51032.9519 | 51586.5038 | 52140.0558 | 52693.6077 | 53247.1596 | 53800.7115 | 54354.2635 | 54907.8154 | 55461.3673 | 56014.9192 | 56568.4712 | 57122.0231 | 57675.575 | 58219.1635 | 58762.7519 | 59306.3404 | 59849.9288 | 60393.5173 | 60937.1058 | 61480.6942 | 62024.2827 | 62567.8712 | 63111.4596 | 63655.0481 | 64198.6365 | 64742.225
N-1 |  | EENS | 11.6 | 34.8 | 65.5667 | 96.3333 | 127.1 | 157.8667 | 188.6333 | 219.4 | 321.975 | 424.55 | 527.125 | 629.7 | 778.9 | 961.5167 | 1144.1333 | 1326.75 | 1509.3667 | 1725.4 | 1997.16 | 2268.92 | 2540.68 | 2812.44 | 3084.2 | 3399.8 | 3715.4 | 4031 | 4346.6 | 4662.2
N-1 |  | IP | 5.7 | 11.1 | 13.9667 | 16.8333 | 19.7 | 22.5667 | 25.4333 | 28.3 | 30.75 | 33.2 | 35.65 | 38.1 | 42.1 | 49 | 55.9 | 62.8 | 69.7 | 79.5 | 79.08 | 78.66 | 78.24 | 77.82 | 77.4 | 90.9 | 104.4 | 117.9 | 131.4 | 144.9
N-1 |  | SAIDI | 0.042384 | 0.15894 | 0.88764 | 1.6163 | 2.345 | 3.0737 | 3.8024 | 4.5311 | 8.8152 | 13.0992 | 17.3833 | 21.6674 | 29.5008 | 46.6295 | 63.7583 | 80.887 | 98.0157 | 124.4397 | 164.5971 | 204.7544 | 244.9118 | 285.0692 | 325.2266 | 389.7102 | 454.1938 | 518.6774 | 583.161 | 647.6446
N-1 |  | SAIFI | 0.010596 | 0.031788 | 0.059915 | 0.088042 | 0.11617 | 0.1443 | 0.17242 | 0.20055 | 0.29596 | 0.39137 | 0.48678 | 0.58219 | 0.72138 | 0.892 | 1.0626 | 1.2333 | 1.4039 | 1.6059 | 1.8633 | 2.1206 | 2.3779 | 2.6352 | 2.8926 | 3.192 | 3.4914 | 3.7909 | 4.0903 | 4.3897
N-1 |  | PFD | 4 | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 27 | 31 | 35 | 39 | 44 | 51 | 58 | 65 | 72 | 81 | 87.6 | 94.2 | 100.8 | 107.4 | 114 | 121.4 | 128.8 | 136.2 | 143.6 | 151
N-1 |  | Deficit Flex-1 | 4238.9824 | 6425.4824 | 8611.9824 | 10798.4824 | 12984.9824 | 15171.4824 | 17357.9824 | 19544.4824 | 21730.9824 | 23917.4824 | 26103.9824 | 28290.4824 | 30476.9824 | 32663.4824 | 34849.9824 | 35619.2872 | 36388.5921 | 37157.8969 | 37927.2017 | 38696.5065 | 39465.8113 | 40235.1161 | 41004.4209 | 41773.7257 | 42543.0305 | 43312.3353 | 44081.6401 | 44850.9449
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 17164.3208 | 19844.0887 | 22754.5274 | 24601.2435 | 26524.5104 | 28541.0948 | 30814.4348 | 33148.2171 | 35561.9498 | 38077.7187 | 40736.7643 | 43501.2116 | 46385.9444 | 49358.9359 | 52298.7216 | 55356.3439 | 58553.2882 | 61842.499 | 65024.8853 | 68293.2688 | 71656.491 | 75060.9515 | 78184.8129 | 81331.7015 | 84513.9878 | 87765.4351 | 90580.7698 | 93440.6833
N-0 |  | EENS (Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS (Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4 | 181.3 | 346.2 | 511.1 | 676 | 1223.92 | 1771.84 | 2319.76 | 2867.68 | 3415.6 | 4332.48 | 5249.36 | 6166.24 | 7083.12 | 8000
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4 | 32.6 | 48.8 | 65 | 81.2 | 97.28 | 113.36 | 129.44 | 145.52 | 161.6 | 175.72 | 189.84 | 203.96 | 218.08 | 232.2
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014254 | 2.5078 | 5.0014 | 7.495 | 9.9885 | 42.4283 | 74.868 | 107.3077 | 139.7475 | 172.1872 | 289.9562 | 407.7251 | 525.4941 | 643.263 | 761.032
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014254 | 0.15758 | 0.30091 | 0.44423 | 0.58756 | 1.0638 | 1.54 | 2.0163 | 2.4925 | 2.9687 | 3.8527 | 4.7367 | 5.6207 | 6.5047 | 7.3887
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 9 | 13 | 17 | 25.2 | 33.4 | 41.6 | 49.8 | 58 | 67 | 76 | 85 | 94 | 103
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170520.8073 | 778286.2861 | 1397881.3832 | 2587242.7038 | 3826509.3712 | 5847822.8094 | 8121525.4796 | 11468360.4732 | 15971435.7541 | 21152202.0528 | 26708333.8182 | 31898121.5325 | 39408806.8112 | 46283322.3774 | 53852029.8042
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020123.7736 | 4440974.2644 | 6878744.8621 | 11771534.6922 | 16626941.1391 | 25893972.8826 | 34984013.0215 | 50354269.3047 | 70580629.2399 | 92924640.3999 | 116716721.0401 | 134422870.6308 | 166042395.6491 | 196113753.3068 | 224787973.3731
N-1 Monetized | Residential | $ | 2477.0702 | 10015.3244 | 17553.5786 | 25091.8328 | 32630.087 | 40168.3412 | 47706.5954 | 55244.8497 | 50980.8962 | 46716.9428 | 42452.9894 | 38189.0359 | 257888.2831 | 367581.3421 | 477274.4011 | 586967.4601 | 696660.5191 | 696347.3899 | 871852.4632 | 1047357.5364 | 1222862.6096 | 1398367.6829 | 1573872.7561 | 1825117.7823 | 2076362.8084 | 2327607.8345 | 2578852.8607 | 2830097.8868
N-1 Monetized | Commercial | $ | 10278.5676 | 41558.4466 | 72838.3256 | 104118.2047 | 135398.0837 | 166677.9627 | 197957.8418 | 229237.7208 | 211544.5064 | 193851.2921 | 176158.0778 | 158464.8634 | 1070103.776 | 1525273.5699 | 1980443.3637 | 2435613.1576 | 2890782.9514 | 2889483.6265 | 3617739.4408 | 4345995.2551 | 5074251.0694 | 5802506.8837 | 6530762.6981 | 7573300.3736 | 8615838.0492 | 9658375.7247 | 10700913.4003 | 11743451.0759
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5110374.2214 | 6015097.5811 | 6967510.5921 | 7745187.9968 | 8491036.7137 | 9233048.7464 | 10172667.8173 | 11216525.0586 | 12260160.0595 | 13330830.0069 | 14604368.7155 | 15898045.9904 | 17328004.7347 | 18766389.6983 | 20232001.0865 | 21817429.4974 | 23600568.0435 | 25503802.0729 | 27434997.0562 | 29443388.6443 | 31566313.1487 | 33843442.2534 | 36000441.2918 | 38358137.1162 | 40806428.0067 | 43292848.4471 | 45372446.2399 | 47951699.3087
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 6657.0645 | Losses (MWh) | 358.8 | 408.65 | 451.6019 | 494.5538 | 537.5058 | 580.4577 | 623.4096 | 666.3615 | 709.3135 | 752.2654 | 795.2173 | 838.1692 | 881.1212 | 924.0731 | 967.025 | 1019.9404 | 1072.8558 | 1125.7712 | 1178.6865 | 1231.6019 | 1284.5173 | 1337.4327 | 1390.3481 | 1443.2635 | 1496.1788 | 1549.0942 | 1602.0096 | 1654.925
| 355383.2586 | Losses ($) | 14352 | 16754.65 | 18978.5708 | 21303.216 | 23732.2319 | 26269.384 | 28918.5611 | 31683.7787 | 34569.1831 | 37579.0553 | 40717.8154 | 43990.0266 | 47400.3997 | 50953.7977 | 54655.2404 | 59087.1116 | 63706.4168 | 68519.7578 | 73533.9494 | 78756.0257 | 84193.2471 | 89853.1071 | 95743.3393 | 101871.9249 | 108247.1002 | 114877.3643 | 121771.4871 | 128938.5178
N-1 | 3417.8021 | EENS | 6.4 | 5.2 | 6.2667 | 7.3333 | 8.4 | 9.4667 | 10.5333 | 11.6 | 26.125 | 40.65 | 55.175 | 69.7 | 209.75 | 316.3833 | 423.0167 | 529.65 | 636.2833 | 709.5 | 1117.81 | 1526.12 | 1934.43 | 2342.74 | 2178.5 | 2657.48 | 3136.46 | 3615.44 | 4094.42 | 4573.4
N-1 | -54.568 | IP | -2.2 | -5.1 | -5.0833 | -5.0667 | -5.05 | -5.0333 | -5.0167 | -5 | -4.5 | -4 | -3.5 | -3 | -2.6 | -5.1 | -7.6 | -10.1 | -12.6 | -18 | -15.6 | -13.2 | -10.8 | -8.4 | -6 | -8.1 | -10.2 | -12.3 | -14.4 | -16.5
N-1 | 635.0181 | SAIDI | 0.16101 | 0.2971 | 0.24476 | 0.19242 | 0.14007 | 0.087731 | 0.035388 | -0.016954 | 0.93827 | 1.8935 | 2.8487 | 3.804 | 24.636 | 36.1727 | 47.7094 | 59.2461 | 70.7829 | 73.0243 | 141.0021 | 208.9798 | 276.9575 | 344.9353 | 412.913 | 587.6467 | 762.3804 | 937.1141 | 1111.8478 | 1286.5815
N-1 | 2.697 | SAIFI | 0.0034097 | -0.00086517 | -0.0023245 | -0.0037839 | -0.0052433 | -0.0067026 | -0.008162 | -0.0096214 | -8.535e-05 | 0.0094507 | 0.018987 | 0.028523 | 0.15102 | 0.24208 | 0.33314 | 0.4242 | 0.51527 | 0.57489 | 0.8374 | 1.0999 | 1.3624 | 1.6249 | 1.8874 | 2.3216 | 2.7557 | 3.1899 | 3.6241 | 4.0583
N-1 | 387.0171 | PFD | 14 | 23 | 25.3333 | 27.6667 | 30 | 32.3333 | 34.6667 | 37 | 40 | 43 | 46 | 49 | 53.8333 | 56.6667 | 59.5 | 62.3333 | 65.1667 | 66 | 70.8 | 75.6 | 80.4 | 85.2 | 90 | 94 | 98 | 102 | 106 | 110
N-1 | 112489.2183 | Flex-1 | 2088.0515 | 3165.0847 | 4242.1179 | 5319.151 | 6396.1842 | 7473.2174 | 8550.2506 | 9627.2837 | 10704.3169 | 11781.3501 | 12858.3832 | 13935.4164 | 15012.4496 | 16089.4828 | 17166.5159 | 19660.7443 | 22154.9727 | 24649.201 | 27143.4294 | 29637.6578 | 32131.8861 | 34626.1145 | 37120.3429 | 39614.5713 | 42108.7996 | 44603.028 | 47097.2564 | 49591.4847
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 625479.561 | Flex-2-2 | 43849.6441 | 47666.1912 | 51623.0473 | 54016.9826 | 56464.4711 | 58848.3085 | 61506.8809 | 64212.3112 | 66996.4044 | 69825.2804 | 72773.518 | 75714.333 | 78717.3741 | 81702.7173 | 84628.6566 | 87572.1253 | 90542.9416 | 93513.3844 | 96262.8354 | 99037.2825 | 101828.9405 | 104676.614 | 107213.1187 | 109729.1881 | 112291.2474 | 114921.1958 | 117146.0692 | 119382.045
N-0 | 16790.5818 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3406.6667 | 3821.15 | 4235.6333 | 4650.1167 | 5064.6 | 5346.08 | 5627.56 | 5909.04 | 6190.52 | 6472 | 6482.08 | 6492.16 | 6502.24 | 6512.32 | 6522.4
N-0 | 1114.1124 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 203.6 | 202.4 | 201.2 | 200 | 198.8 | 196.4 | 194 | 191.6 | 189.2 | 186.8 | 185.12 | 183.44 | 181.76 | 180.08 | 178.4
N-0 | 1469.8767 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9475 | 252.8531 | 305.7586 | 358.6642 | 411.5698 | 509.4889 | 607.408 | 705.3271 | 803.2461 | 901.1652 | 1007.6687 | 1114.1721 | 1220.6756 | 1327.179 | 1433.6825
N-0 | 18.6232 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6288 | 4.1021 | 4.5754 | 5.0487 | 5.522 | 5.9284 | 6.3349 | 6.7414 | 7.1479 | 7.5543 | 7.6569 | 7.7594 | 7.862 | 7.9645 | 8.0671
N-0 | 212.762 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 46.6667 | 48 | 49.3333 | 50.6667 | 52 | 50.4 | 48.8 | 47.2 | 45.6 | 44 | 43 | 42 | 41 | 40 | 39
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 1998483.6243 | 187.1022 | -3318.6679 | -2257.4366 | -1196.2054 | -134.9742 | 926.2571 | 1987.4883 | 3048.7196 | 54874.0272 | 106699.3348 | 158524.6424 | 210349.95 | 134649.3724 | 168954.9829 | 203260.5935 | 237566.204 | 271871.8145 | 416183.6132 | 585100.0335 | 754016.4539 | 922932.8743 | 1091849.2947 | 1260765.7151 | 1563422.4878 | 1866079.2605 | 2168736.0331 | 2471392.8058 | 2774049.5785
Commerical(N-1) | EENS | 8292679.4782 | 776.3778 | -13770.7654 | -9367.2014 | -4963.6373 | -560.0733 | 3843.4907 | 8247.0547 | 12650.6187 | 227698.9982 | 442747.3777 | 657795.7573 | 872844.1368 | 558725.6627 | 701076.3074 | 843426.9521 | 985777.5968 | 1128128.2415 | 1726948.005 | 2427864.2977 | 3128780.5904 | 3829696.8831 | 4530613.1758 | 5231529.4685 | 6487399.4577 | 7743269.447 | 8999139.4362 | 10255009.4255 | 11510879.4147
Aggregate | EENS | 10291163.1025 | 963.48 | -17089.4332 | -11624.638 | -6159.8427 | -695.0475 | 4769.7478 | 10234.543 | 15699.3383 | 282573.0254 | 549446.7126 | 816320.3997 | 1083194.0868 | 693375.0352 | 870031.2904 | 1046687.5456 | 1223343.8008 | 1400000.056 | 2143131.6182 | 3012964.3313 | 3882797.0443 | 4752629.7574 | 5622462.4705 | 6492295.1836 | 8050821.9455 | 9609348.7074 | 11167875.4694 | 12726402.2313 | 14284928.9932
Residential (N-0) | EENS | 96402545.7073 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17695946.1494 | 20218511.5 | 23300217.605 | 26253074.6379 | 29714707.9822 | 32623251.3185 | 36416570.0176 | 38596786.9813 | 40056175.4644 | 40800814.8742 | 41483742.6746 | 43855454.5223 | 44664089.964 | 44012832.3579 | 46089292.1213
Commerical(N-0) | EENS | 412520351.241 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 76655071.337 | 85951569.3017 | 99816223.8937 | 112573831.4187 | 127085490.3728 | 138664373.5468 | 155748490.3483 | 161382226.4515 | 167060241.051 | 168099643.0325 | 168694107.645 | 181966441.7211 | 185484423.8183 | 175922427.0598 | 180365012.189
Aggregate | EENS | 508922896.9483 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 94351017.4864 | 106170080.8016 | 123116441.4987 | 138826906.0566 | 156800198.355 | 171287624.8653 | 192165060.3659 | 199979013.4327 | 207116416.5154 | 208900457.9066 | 210177850.3196 | 225821896.2433 | 230148513.7824 | 219935259.4177 | 226454304.3103
Residential (N-1) | Value for Flex-1 | 635671269.5836 | 8238114.0347 | 12799582.0479 | 17583974.6405 | 22599587.1239 | 27854990.2474 | 33359038.7851 | 39120880.3807 | 45149964.6569 | 51456052.5967 | 58049226.2056 | 64939898.462 | 72138823.5649 | 79657107.4864 | 87506218.8392 | 95698000.0675 | 112342613.0852 | 129759645.5037 | 147977315.41 | 167024769.0332 | 186932109.5153 | 207730426.541 | 229451826.8495 | 252129465.6568 | 275797579.0127 | 300491517.1204 | 326247778.6465 | 353104046.0508 | 381099221.9637
Commerical(N-1) | Value for Flex-1 | 2618732030.6971 | 33938002.4352 | 52729574.3762 | 72439513.6626 | 93101993.9295 | 114752323.5136 | 137426980.8307 | 161163650.8115 | 186001262.4283 | 211980027.3442 | 239141479.7169 | 267528517.1911 | 297185443.1142 | 328158010.0103 | 360493464.3491 | 394240592.6487 | 462810281.6273 | 534562054.6845 | 609612159.9685 | 688080669.2325 | 770091596.3597 | 855773019.425 | 945257206.3959 | 1038680744.5782 | 1136184673.9155 | 1237914624.2544 | 1344020956.6891 | 1454658909.1053 | 1569988746.0444
Aggregate | Value for Flex-1 | 3254403300.2807 | 42176116.4699 | 65529156.424 | 90023488.3031 | 115701581.0534 | 142607313.761 | 170786019.6158 | 200284531.1923 | 231151227.0853 | 263436079.941 | 297190705.9225 | 332468415.6531 | 369324266.6791 | 407815117.4966 | 447999683.1883 | 489938592.7162 | 575152894.7125 | 664321700.1882 | 757589475.3784 | 855105438.2656 | 957023705.875 | 1063503445.966 | 1174709033.2454 | 1290810210.235 | 1411982252.9283 | 1538406141.3748 | 1670268735.3356 | 1807762955.1561 | 1951087968.008
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 201421523.7425 | 11415404.7265 | 12677256.0862 | 14005928.335 | 14898443.9956 | 16001404.1511 | 17079540.6575 | 18025564.8207 | 19173409.5383 | 20408716.3778 | 21700257.5548 | 23225050.5217 | 24562337.3095 | 26000278.4294 | 27628571.2119 | 29216356.1057 | 31019684.7629 | 32721790.7961 | 34498473.5373 | 36216597.8881 | 38085174.9541 | 39829235.0504 | 41537971.8595 | 43666848.8026 | 45674640.5094 | 47592810.1302 | 49813062.131 | 52005419.7536 | 54190723.0631
Aggregate ($M) |  | 3975.0389 | 55531024.7188 | 83283168.9217 | 111758934.5329 | 141395626.9326 | 171590282.8534 | 202502041.1694 | 237849021.5787 | 274488040.3429 | 314482422.7478 | 359785782.9883 | 409456389.6453 | 463310621.1901 | 518493178.9885 | 570849303.177 | 626371717.1691 | 730512364.7749 | 837270397.0969 | 951031278.8889 | 1065622625.3503 | 1191156738.2394 | 1308064324.2066 | 1428985884.0908 | 1549869812.1279 | 1675885565.7028 | 1821430196.4558 | 1961398186.7184 | 2092430036.5586 | 2246017924.3746
Aggregate ($M)+ Monetized Losses |  | 3975.3943 | 55545376.7188 | 83299923.5717 | 111777913.1037 | 141416930.1487 | 171614015.0853 | 202528310.5534 | 237877940.1398 | 274519724.1216 | 314516991.9309 | 359823362.0436 | 409497107.4606 | 463354611.2167 | 518540579.3882 | 570900256.9747 | 626426372.4095 | 730571451.8864 | 837334103.5137 | 951099798.6467 | 1065696159.2997 | 1191235494.2651 | 1308148517.4537 | 1429075737.1979 | 1549965555.4671 | 1675987437.6276 | 1821538443.5559 | 1961513064.0826 | 2092551808.0458 | 2246146862.8924
Project Cost |  | 400
Benefit-Cost Ratio |  | 9.9385
Market Participation Revenue (All costs are $x1,000) |  |  | 2036: 4200.5673; 2037: 5051.1321; 2038: 5901.6968; 2039: 6752.2616; 2040: 7602.8263; 2041: 8453.391; 2042: 8851.8081; 2043: 9250.2252; 2044: 9648.6423; 2045: 10047.0594; 2046: 10445.4765; 2047: 10561.0575; 2048: 10676.6384

## SDG&E and Central BESS in VS
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| SDG&E and Centralized BESS in Valley South | Losses (MWh) | 44182.4 | 44715.005 | 45093.4314 | 45471.8578 | 45850.2842 | 46228.7106 | 46607.137 | 46985.5634 | 47363.9897 | 47742.4161 | 48120.8425 | 48499.2689 | 48877.6953 | 49249.2036 | 49620.7119 | 49992.2201 | 50363.7284 | 50735.2367 | 51106.745 | 51478.2533 | 51849.7615 | 52221.2698 | 52592.7781 | 52964.2864 | 53335.7947 | 53707.3029 | 54078.8112 | 54450.3195
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | Deficit Flex-1 | 2696.9807 | 5667.5888 | 7543.2787 | 9418.9686 | 11294.6585 | 13170.3483 | 15046.0382 | 16921.7281 | 18797.418 | 20673.1079 | 22548.7978 | 24424.4877 | 26300.1776 | 28175.8675 | 30051.5574 | 31927.2473 | 33802.9371 | 35678.627 | 37554.3169 | 37854.6503 | 38154.9837 | 38455.317 | 38755.6504 | 39055.9837 | 39356.3171 | 39656.6505 | 39956.9838 | 40257.3172
N-1 |  | Deficit Flex-2-1 | 58391.3519 | 60909.1505 | 63468.7534 | 65012.9523 | 66580.8234 | 68152.8622 | 69883.551 | 71621.9247 | 73383.2755 | 75162.7501 | 76998.3621 | 78847.7006 | 80725.5882 | 82598.7507 | 84416.5313 | 86236.7121 | 88071.4543 | 89891.6351 | 91580.7628 | 93269.8906 | 94959.0183 | 96633.5846 | 98133.4135 | 99618.681 | 101103.9485 | 102603.7775 | 103870.6233 | 105137.4691
N-1 |  | Deficit Flex-2-2 | 13056.4521 | 15232.4908 | 17633.376 | 19168.7768 | 20799.3444 | 22493.1163 | 24426.8606 | 26412.5649 | 28514.2344 | 30698.9165 | 33011.4003 | 35402.8386 | 37912.6384 | 40486.0614 | 43070.2782 | 45740.9464 | 48535.5399 | 51366.9248 | 54079.0544 | 56865.7318 | 59745.092 | 62682.8822 | 65409.9104 | 68165.9418 | 70986.2028 | 73871.0866 | 76355.4176 | 78883.4913
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 3966989.8423 | 4707050.0965 | 5543241.2374 | 6095692.5942 | 6811876.7156 | 7457565.859 | 8272370.8013 | 9159673.3031 | 9932379.814 | 10912742.266 | 12065920.7978 | 13154935.4186 | 14285891.8348 | 15646720.8149 | 16958054.5979 | 18437737.9304 | 19885747.6023 | 21543950.1016 | 22934114.7932 | 24733588.4445 | 26583755.411 | 28522121.9107 | 30500906.1181 | 32447439.8292 | 34585804.0493 | 36812303.0186 | 38950786.8712 | 41143738.4275
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 71526.7454 | Losses (MWh) | 5899.35 | 6173.045 | 6391.1225 | 6609.1999 | 6827.2774 | 7045.3548 | 7263.4323 | 7481.5097 | 7699.5872 | 7917.6646 | 8135.7421 | 8353.8195 | 8571.897 | 8796.8926 | 9021.8881 | 9246.8837 | 9471.8793 | 9696.8748 | 9921.8704 | 10146.866 | 10371.8615 | 10596.8571 | 10821.8527 | 11046.8482 | 11271.8438 | 11496.8394 | 11721.8349 | 11946.8305
| 3659341.452 | Losses ($) | 235974 | 253094.845 | 268586.9211 | 284695.4168 | 301441.4705 | 318846.8921 | 336934.184 | 355726.5611 | 375247.9732 | 395523.1269 | 416577.5082 | 438437.4066 | 461129.939 | 485064.5425 | 509907.6699 | 535689.7884 | 562442.3205 | 590197.6731 | 618989.2668 | 648851.5667 | 679820.1133 | 711931.555 | 745223.6812 | 779735.4565 | 815507.0558 | 852579.9003 | 890996.6952 | 930801.4674
N-1 | 9653.5934 | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 | 265.9402 | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 | 1137.6463 | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 | 8.5082 | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 | 703.6435 | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-1 | 133288.857 | Flex-1 | 3630.0532 | 3922.9784 | 5310.8216 | 6698.6649 | 8086.5082 | 9474.3515 | 10862.1948 | 12250.038 | 13637.8813 | 15025.7246 | 16413.5679 | 17801.4112 | 19189.2544 | 20577.0977 | 21964.941 | 23352.7843 | 24740.6276 | 26128.4709 | 27516.3141 | 30479.5139 | 33442.7137 | 36405.9136 | 39369.1134 | 42332.3132 | 45295.513 | 48258.7128 | 51221.9126 | 54185.1124
N-1 | 1302863.5904 | Flex-2-1 | 136221.1839 | 137060.5368 | 137858.0854 | 138307.7277 | 138750.7392 | 139172.5416 | 139606.1077 | 140014.9477 | 140400.8105 | 140768.5495 | 141131.2753 | 141480.2745 | 141817.766 | 142142.9414 | 142455.3329 | 142765.3244 | 143077.7958 | 143387.7873 | 143675.4594 | 143963.1315 | 144250.8036 | 144535.9957 | 144791.4287 | 145044.3818 | 145297.3348 | 145552.7678 | 145768.5219 | 145984.2759
N-1 | 691943.5847 | Flex-2-2 | 47957.5128 | 52277.7891 | 56744.1988 | 59449.4493 | 62189.6372 | 64896.287 | 67894.4551 | 70947.9633 | 74044.1199 | 77204.0826 | 80498.882 | 83812.706 | 87190.6802 | 90575.5919 | 93857.1 | 97187.5228 | 100560.6899 | 103988.9587 | 107208.6663 | 110464.8196 | 113740.3395 | 117054.6832 | 119988.0212 | 122894.9478 | 125819.0324 | 128815.5443 | 131371.4214 | 133939.2369
N-0 | 21183.8076 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 | 1335.7024 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 | 1756.8124 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 | 22.5453 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 | 284.3733 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 4652002.7758 | 2664.1723 | 6696.6565 | 15296.142 | 23895.6274 | 32495.1129 | 41094.5983 | 49694.0838 | 58293.5692 | 105854.9234 | 153416.2776 | 200977.6318 | 248538.986 | 392537.6555 | 536536.325 | 680534.9945 | 824533.664 | 968532.3336 | 1112531.0031 | 1456952.4967 | 1801373.9903 | 2145795.484 | 2490216.9776 | 2834638.4712 | 3388540.27 | 3942442.0689 | 4496343.8677 | 5050245.6665 | 5604147.4653
Commerical(N-1) | EENS | 19303419.5944 | 11054.9454 | 27787.6812 | 63471.1243 | 99154.5673 | 134838.0103 | 170521.4534 | 206204.8964 | 241888.3395 | 439243.5047 | 636598.6698 | 833953.835 | 1031309.0002 | 1628829.4388 | 2226349.8773 | 2823870.3159 | 3421390.7544 | 4018911.193 | 4616431.6315 | 6045603.7385 | 7474775.8455 | 8903947.9525 | 10333120.0595 | 11762292.1666 | 14060699.8314 | 16359107.4962 | 18657515.161 | 20955922.8258 | 23254330.4906
Aggregate | EENS | 23955422.3702 | 13719.1178 | 34484.3377 | 78767.2662 | 123050.1947 | 167333.1232 | 211616.0517 | 255898.9802 | 300181.9087 | 545098.4281 | 790014.9475 | 1034931.4668 | 1279847.9862 | 2021367.0943 | 2762886.2023 | 3504405.3104 | 4245924.4184 | 4987443.5265 | 5728962.6346 | 7502556.2352 | 9276149.8359 | 11049743.4365 | 12823337.0371 | 14596930.6378 | 17449240.1014 | 20301549.565 | 23153859.0286 | 26006168.4922 | 28858477.9559
Residential (N-0) | EENS | 122402385.4505 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7548985.0744 | 9794691.5976 | 12474348.3757 | 15347020.984 | 17866466.9567 | 20996797.7861 | 24698098.9882 | 28840317.3417 | 33541217.3533 | 38471074.1279 | 44538095.4972 | 50065147.4545 | 56027611.2185 | 61953016.927 | 68192076.4928 | 75753576.0548 | 84072896.7752 | 90296154.7352 | 99941321.9255
Commerical(N-0) | EENS | 524690134.185 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32796387.724 | 43151911.473 | 55866474.7388 | 68637387.0433 | 77675195.1106 | 90392543.5661 | 106694968.7558 | 124345366.1109 | 143712431.512 | 164558346.4294 | 190732503.3698 | 211736495.7562 | 237640870.2909 | 261024283.4324 | 285410828.6852 | 316389312.3519 | 351526819.4674 | 372036180.3666 | 405152985.562
Aggregate | EENS | 647092519.6355 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 40345372.7984 | 52946603.0707 | 68340823.1146 | 83984408.0273 | 95541662.0673 | 111389341.3522 | 131393067.744 | 153185683.4525 | 177253648.8653 | 203029420.5574 | 235270598.867 | 261801643.2106 | 293668481.5094 | 322977300.3594 | 353602905.1779 | 392142888.4066 | 435599716.2426 | 462332335.1019 | 505094307.4875
Residential (N-1) | Value for Flex-1 | 741628773.859 | 14321865.1177 | 15864499.0795 | 22013851.5198 | 28460756.2702 | 35216247.6009 | 42291725.5255 | 49698967.1916 | 57450138.6125 | 65557806.75 | 74034951.9577 | 82894980.7966 | 92151739.2324 | 101819526.2271 | 111913107.7344 | 122447731.1133 | 133439139.9687 | 144903589.435 | 156857861.9121 | 169319283.2697 | 192241906.5935 | 216204836.5315 | 241245761.7749 | 267403605.2575 | 294718562.3131 | 323232139.9683 | 352987197.4048 | 384027987.6256 | 416400200.3591
Commerical(N-1) | Value for Flex-1 | 3055238010.4633 | 59000821.207 | 65355906.2337 | 90688978.4898 | 117247856.9173 | 145077998.6547 | 174226367.5683 | 204741481.1785 | 236673458.9894 | 270074072.2652 | 304996795.2928 | 341496858.1767 | 379631301.2077 | 419459030.854 | 461040877.4192 | 504439654.4185 | 549720219.7193 | 596949538.5012 | 646196748.0848 | 697533224.6861 | 791966009.0483 | 890684474.3631 | 993843884.1881 | 1101604586.7078 | 1214132171.926 | 1331597633.5383 | 1454177535.6238 | 1582054184.2926 | 1715415804.435
Aggregate | Value for Flex-1 | 3796866784.3223 | 73322686.3247 | 81220405.3131 | 112702830.0096 | 145708613.1875 | 180294246.2556 | 216518093.0938 | 254440448.37 | 294123597.6019 | 335631879.0151 | 379031747.2505 | 424391838.9733 | 471783040.4402 | 521278557.081 | 572953985.1537 | 626887385.5318 | 683159359.688 | 741853127.9362 | 803054609.9969 | 866852507.9557 | 984207915.6418 | 1106889310.8947 | 1235089645.963 | 1369008191.9653 | 1508850734.2391 | 1654829773.5066 | 1807164733.0285 | 1966082171.9181 | 2131816004.7941
Residential (N-1) | Value for Flex-2 | 53721266.0105 | 4535568.7122 | 4677603.3727 | 4822442.6719 | 4959125.9963 | 5099385.7651 | 5242760.101 | 5390570.267 | 5541515.6043 | 5695706.9753 | 5853390.8489 | 6015185.4315 | 6180811.7053 | 6350444.4996 | 6524130.6326 | 6701930.6205 | 6884427.2906 | 7071982.6644 | 7264487.3985 | 7461038.3389 | 7662876.5216 | 7870143.4645 | 8082845.7721 | 8299558.5358 | 8521909.4536 | 8750190.6932 | 8984712.8831 | 9222981.7723 | 9467548.6604
Commerical(N-1) | Value for Flex-2 | 242156769.7251 | 20444765.1699 | 21085007.9849 | 21737893.1348 | 22354013.9892 | 22986256.2105 | 23632537.8157 | 24298814.5995 | 24979223.6439 | 25674264.6791 | 26385048.7001 | 27114362.3664 | 27860947.9631 | 28625593.5598 | 29408510.1968 | 30209970.6597 | 31032602.1312 | 31878036.4787 | 32745780.8198 | 33631764.05 | 34541580.3288 | 35475867.569 | 36434655.5419 | 37411521.2545 | 38413801.8037 | 39442814.1796 | 40499958.5875 | 41573991.8115 | 42676414.2226
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 295878035.7356 | 24980333.8822 | 25762611.3576 | 26560335.8067 | 27313139.9855 | 28085641.9756 | 28875297.9166 | 29689384.8666 | 30520739.2482 | 31369971.6544 | 32238439.549 | 33129547.798 | 34041759.6683 | 34976038.0594 | 35932640.8293 | 36911901.2802 | 37917029.4218 | 38950019.1431 | 40010268.2183 | 41092802.3889 | 42204456.8504 | 43346011.0334 | 44517501.314 | 45711079.7903 | 46935711.2573 | 48193004.8728 | 49484671.4706 | 50796973.5838 | 52143962.883
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 224127689.7039 | 12558789.1056 | 13985303.5709 | 15430197.6897 | 16547939.3982 | 17680564.1492 | 18855023.5449 | 19925861.8368 | 21230261.2938 | 22736496.6233 | 24118345.2956 | 25763498.4394 | 27305447.8813 | 29042391.3293 | 30748240.0953 | 32490302.5944 | 34399376.3299 | 36436611.2374 | 38458325.5086 | 40717480.1511 | 42794975.1539 | 44811792.788 | 46859292.2022 | 49166383.9763 | 51585337.7964 | 53813434.0876 | 56293607.5595 | 58427079.1222 | 60998683.9443
Aggregate ($M) |  | 4987.9205 | 112814068.4727 | 126096650.4241 | 162513273.305 | 200494504.4923 | 239210045.4924 | 279091741.7554 | 323840285.0762 | 370322484.4336 | 420638499.1246 | 476523919.841 | 537266419.7481 | 602750919.0905 | 671302761.5913 | 737939414.3479 | 811183336.0689 | 891114757.6022 | 975412885.2957 | 1064505815.2237 | 1159194767.2883 | 1313754096.3489 | 1467898501.3633 | 1632958258.0257 | 1801459886.7291 | 1978423928.5721 | 2169280650.4386 | 2371696587.3299 | 2563644728.2182 | 2778911437.0648
Aggregate ($M)+ Monetized Losses |  | 4991.5798 | 113050042.4727 | 126349745.2691 | 162781860.2261 | 200779199.9091 | 239511486.9628 | 279410588.6475 | 324177219.2602 | 370678210.9947 | 421013747.0978 | 476919442.9679 | 537682997.2563 | 603189356.4972 | 671763891.5303 | 738424478.8904 | 811693243.7388 | 891650447.3906 | 975975327.6161 | 1065096012.8967 | 1159813756.5551 | 1314402947.9156 | 1468578321.4766 | 1633670189.5807 | 1802205110.4103 | 1979203664.0286 | 2170096157.4943 | 2372549167.2302 | 2564535724.9134 | 2779842238.5321
Project Cost |  | 701
Benefit-Cost Ratio |  | 7.1207
Market Participation Revenue (All costs are $x1,000) |  |  | 2034: 4243.9732; 2035: 5387.0046; 2036: 6530.036; 2037: 7673.0673; 2038: 8816.0987; 2039: 9729.2914; 2040: 10642.4841; 2041: 11555.6768; 2042: 12468.8694; 2043: 13382.0621; 2044: 13535.6757; 2045: 13689.2892; 2046: 13842.9028; 2047: 13996.5163; 2048: 14150.1298

## Valley South to Valley North
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50081.75 | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 18 | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 3.5 | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.2034 | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.014006 | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 18 | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-0 |  | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
N-1 |  | Deficit Flex-1 | 6327.034 | 9590.5671 | 12854.1003 | 16117.6335 | 19381.1667 | 22644.6998 | 25908.233 | 29171.7662 | 32435.2993 | 35698.8325 | 38962.3657 | 42225.8989 | 45489.432 | 48752.9652 | 52016.4984 | 55280.0315 | 58543.5647 | 61807.0979 | 65070.6311 | 68334.1642 | 71597.6974 | 74861.2306 | 78124.7637 | 81388.2969 | 84651.8301 | 87915.3633 | 91178.8964 | 94442.4296
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 61013.9649 | 67510.2799 | 74377.5747 | 78618.226 | 82988.9815 | 87389.4033 | 92321.3156 | 97360.5282 | 102558.3543 | 107902.9991 | 113510.2823 | 119215.5446 | 125103.3185 | 131061.6532 | 136927.3781 | 142928.4692 | 149096.2298 | 155355.8834 | 161287.7207 | 167330.5514 | 173485.4315 | 179737.5655 | 185397.9316 | 191060.8896 | 196805.2352 | 202686.6309 | 207726.839 | 212822.7283
|  | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Valley South to Valley North | Losses (MWh) | 49722.95 | 50479.4 | 51032.9519 | 51586.5038 | 52140.0558 | 52693.6077 | 53247.1596 | 53800.7115 | 54354.2635 | 54907.8154 | 55461.3673 | 56014.9192 | 56568.4712 | 57122.0231 | 57675.575 | 58229.1269 | 58782.6788 | 59336.2308 | 59889.7827 | 60443.3346 | 60996.8865 | 61550.4385 | 62103.9904 | 62657.5423 | 63211.0942 | 63764.6462 | 64318.1981 | 64871.75
N-1 |  | EENS | 12.4 | 31.9 | 62.6333 | 93.3667 | 124.1 | 154.8333 | 185.5667 | 216.3 | 328.58 | 440.86 | 553.14 | 665.42 | 777.7 | 1050.86 | 1324.02 | 1597.18 | 1870.34 | 2143.5 | 2618.12 | 3092.74 | 3567.36 | 4041.98 | 4516.6 | 5149.78 | 5782.96 | 6416.14 | 7049.32 | 7682.5
N-1 |  | IP | 5.9 | 10.3 | 13.3 | 16.3 | 19.3 | 22.3 | 25.3 | 28.3 | 31.04 | 33.78 | 36.52 | 39.26 | 42 | 45.18 | 48.36 | 51.54 | 54.72 | 57.9 | 61.76 | 65.62 | 69.48 | 73.34 | 77.2 | 88.76 | 100.32 | 111.88 | 123.44 | 135
N-1 |  | SAIDI | 0.045307 | 0.1457 | 0.86574 | 1.5858 | 2.3058 | 3.0259 | 3.7459 | 4.466 | 9.4602 | 14.4544 | 19.4486 | 24.4428 | 29.437 | 54.6278 | 79.8186 | 105.0094 | 130.2001 | 155.3909 | 225.1752 | 294.9596 | 364.7439 | 434.5282 | 504.3125 | 637.5894 | 770.8663 | 904.1432 | 1037.4201 | 1170.697
N-1 |  | SAIFI | 0.011327 | 0.029139 | 0.057236 | 0.085333 | 0.11343 | 0.14153 | 0.16962 | 0.19772 | 0.30223 | 0.40674 | 0.51126 | 0.61577 | 0.72028 | 0.97704 | 1.2338 | 1.4905 | 1.7473 | 2.0041 | 2.4538 | 2.9035 | 3.3532 | 3.803 | 4.2527 | 4.8525 | 5.4524 | 6.0522 | 6.652 | 7.2519
N-1 |  | PFD | 4 | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 27.2 | 31.4 | 35.6 | 39.8 | 44 | 52.6 | 61.2 | 69.8 | 78.4 | 87 | 95.4 | 103.8 | 112.2 | 120.6 | 129 | 138.8 | 148.6 | 158.4 | 168.2 | 178
N-1 |  | Deficit Flex-1 | 4238.9824 | 6425.4824 | 8611.9824 | 10798.4824 | 12984.9824 | 15171.4824 | 17357.9824 | 19544.4824 | 21730.9824 | 23917.4824 | 26103.9824 | 28290.4824 | 30476.9824 | 32663.4824 | 34849.9824 | 37036.4824 | 39222.9825 | 41409.4825 | 43595.9825 | 45782.4825 | 47968.9825 | 50155.4825 | 52341.9825 | 54528.4825 | 56714.9825 | 58901.4825 | 61087.9825 | 63274.4825
N-1 |  | Deficit Flex-2-1 | 194612.5358 | 197969.6873 | 201326.8387 | 203320.68 | 205331.5626 | 207325.4038 | 209489.6588 | 211636.8724 | 213784.086 | 215931.2996 | 218129.6374 | 220327.9751 | 222543.3543 | 224741.692 | 226871.8642 | 229002.0365 | 231149.2501 | 233279.4223 | 235256.2222 | 237233.022 | 239209.8219 | 241169.5803 | 242924.8422 | 244663.0628 | 246401.2833 | 248156.5453 | 249639.1451 | 251121.745
N-1 |  | Deficit Flex-2-2 | 17164.3208 | 19844.0887 | 22754.5274 | 24601.2435 | 26524.5104 | 28541.0948 | 30814.4348 | 33148.2171 | 35561.9498 | 38077.7187 | 40736.7643 | 43501.2116 | 46385.9444 | 49358.9359 | 52298.7216 | 55356.3439 | 58553.2882 | 61842.499 | 65024.8853 | 68293.2688 | 71656.491 | 75060.9515 | 78184.8129 | 81331.7015 | 84513.9878 | 87765.4351 | 90580.7698 | 93440.6833
N-0 |  | EENS(Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 42.15 | 79.5 | 149 | 218.5 | 288 | 357.5 | 427 | 542.18 | 657.36 | 772.54 | 887.72 | 1002.9
N-0 |  | EENS(Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.15 | 152.3 | 228.45 | 304.6 | 721.28 | 1137.96 | 1554.64 | 1971.32 | 2388 | 3345.9467 | 4303.8933 | 5261.84 | 6219.7867 | 7719 | 8977.5164 | 10236.0327 | 11494.5491 | 12753.0655 | 15815
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 27.8 | 41.7 | 55.6 | 72.96 | 90.32 | 107.68 | 125.04 | 173 | 200.46 | 227.92 | 255.38 | 282.84 | 309.6 | 335.1018 | 360.6036 | 386.1055 | 411.6073 | 432.8
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1631 | 2.3261 | 3.4892 | 4.6523 | 31.7777 | 58.9032 | 86.0286 | 113.1541 | 140.6941 | 268.1142 | 395.5343 | 522.9544 | 650.3745 | 876.9103 | 1122.7973 | 1368.6842 | 1614.5711 | 1860.4581 | 2797.2719
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15173 | 0.30347 | 0.4552 | 0.60693 | 1.0467 | 1.4864 | 1.9261 | 2.3659 | 2.8747 | 4.0513 | 5.2278 | 6.4044 | 7.581 | 9.434 | 10.4946 | 11.5552 | 12.6159 | 13.6765 | 13.8033
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.25 | 6.5 | 9.75 | 13 | 20.4 | 27.8 | 35.2 | 42.6 | 56 | 65.3 | 74.6 | 83.9 | 93.2 | 104 | 115.2727 | 126.5455 | 137.8182 | 149.0909 | 165
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121943.8344 | 557395.4427 | 1230664.8375 | 2104893.335 | 3208711.836 | 5074358.4432 | 7356481.1197 | 10946144.5435 | 15806399.7042 | 21496447.9969 | 27112613.0824 | 34384929.452 | 42810474.2398 | 51429515.327 | 61762709.9299 | 72801144.7123 | 85069521.1424 | 97078203.8763 | 109941014.3618
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729516.8638 | 3180050.4533 | 6467576.6035 | 9571528.7893 | 13952844.5382 | 22407387.6493 | 31774221.803 | 48563777.1925 | 70557078.1079 | 95534054.1264 | 116645008.9635 | 146394121.4309 | 182921292.1372 | 217158766.2423 | 259884344.5265 | 305303925.3443 | 356576854.9237 | 403428367.1589 | 455603388.6507
N-1 Monetized | Residential | $ | 2647.9026 | 10044.4024 | 17440.9022 | 24837.402 | 32233.9018 | 39630.4016 | 47026.9014 | 54423.4012 | 95034.2273 | 135645.0533 | 176255.8794 | 216866.7054 | 257477.5314 | 381974.2392 | 506470.9469 | 630967.6546 | 755464.3623 | 879961.07 | 1146479.2724 | 1412997.4748 | 1679515.6772 | 1946033.8796 | 2212552.082 | 2636500.642 | 3060449.2021 | 3484397.7621 | 3908346.3221 | 4332294.8821
N-1 Monetized | Commercial | $ | 10987.4343 | 41676.7166 | 72365.9989 | 103055.2813 | 133744.5636 | 164433.8459 | 195123.1283 | 225812.4106 | 394329.8021 | 562847.1935 | 731364.585 | 899881.9765 | 1068399.368 | 1584996.6924 | 2101594.0168 | 2618191.3412 | 3134788.6657 | 3651385.9901 | 4757299.4941 | 5863212.9981 | 6969126.5022 | 8075040.0062 | 9180953.5102 | 10940122.0522 | 12699290.5941 | 14458459.1361 | 16217627.6781 | 17976796.22
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5110374.2214 | 6015097.5811 | 6967510.5921 | 7745187.9968 | 8491036.7137 | 9233048.7464 | 10172667.8173 | 11216525.0586 | 12260160.0595 | 13330830.0069 | 14604368.7155 | 15898045.9904 | 17328004.7347 | 18766389.6983 | 20232001.0865 | 21817429.4974 | 23600568.0435 | 25503802.0729 | 27434997.0562 | 29443388.6443 | 31566313.1487 | 33843442.2534 | 36000441.2918 | 38358137.1162 | 40806428.0067 | 43292848.4471 | 45372446.2399 | 47951699.3087
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117 | 77.912
Comparison to Baseline
| NPV of benefit | Component | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 6560.5113 | Losses (MWh) | 358.8 | 408.65 | 451.6019 | 494.5538 | 537.5058 | 580.4577 | 623.4096 | 666.3615 | 709.3135 | 752.2654 | 795.2173 | 838.1692 | 881.1212 | 924.0731 | 967.025 | 1009.9769 | 1052.9288 | 1095.8808 | 1138.8327 | 1181.7846 | 1224.7365 | 1267.6885 | 1310.6404 | 1353.5923 | 1396.5442 | 1439.4962 | 1482.4481 | 1525.4
| 348715.3314 | Losses ($) | 14352 | 16754.65 | 18978.5708 | 21303.216 | 23732.2319 | 26269.384 | 28918.5611 | 31683.7787 | 34569.1831 | 37579.0553 | 40717.8154 | 43990.0266 | 47400.3997 | 50953.7977 | 54655.2404 | 58509.909 | 62523.1516 | 66700.4876 | 71047.6135 | 75570.4078 | 80274.9371 | 85167.4613 | 90254.4399 | 95542.5378 | 101038.6316 | 106749.816 | 112683.4104 | 118846.9659
N-1 | 1471.0441 | EENS | 5.6 | 8.1 | 9.2 | 10.3 | 11.4 | 12.5 | 13.6 | 14.7 | 19.52 | 24.34 | 29.16 | 33.98 | 210.95 | 227.04 | 243.13 | 259.22 | 275.31 | 291.4 | 496.85 | 702.3 | 907.75 | 1113.2 | 746.1 | 907.5 | 1068.9 | 1230.3 | 1391.7 | 1553.1
N-1 | -32.719 | IP | -2.4 | -4.3 | -4.4167 | -4.5333 | -4.65 | -4.7667 | -4.8833 | -5 | -4.79 | -4.58 | -4.37 | -4.16 | -2.5 | -1.28 | -0.06 | 1.16 | 2.38 | 3.6 | 1.72 | -0.16 | -2.04 | -3.92 | -5.8 | -5.96 | -6.12 | -6.28 | -6.44 | -6.6
N-1 | 374.1303 | SAIDI | 0.15809 | 0.31035 | 0.26665 | 0.22296 | 0.17926 | 0.13557 | 0.091871 | 0.048175 | 0.29325 | 0.53833 | 0.78341 | 1.0285 | 24.6997 | 28.1744 | 31.6491 | 35.1238 | 38.5984 | 42.0731 | 80.4239 | 118.7747 | 157.1254 | 195.4762 | 233.827 | 339.7674 | 445.7078 | 551.6482 | 657.5886 | 763.529
N-1 | 0.84873 | SAIFI | 0.0026789 | 0.0017839 | 0.00035493 | -0.001074 | -0.0025029 | -0.0039318 | -0.0053607 | -0.0067897 | -0.0063576 | -0.0059256 | -0.0054935 | -0.0050615 | 0.15211 | 0.15705 | 0.16198 | 0.16691 | 0.17184 | 0.17678 | 0.24687 | 0.31697 | 0.38707 | 0.45717 | 0.52727 | 0.66104 | 0.79481 | 0.92857 | 1.0623 | 1.1961
N-1 | 364.9905 | PFD | 14 | 23 | 25.3333 | 27.6667 | 30 | 32.3333 | 34.6667 | 37 | 39.8 | 42.6 | 45.4 | 48.2 | 53.8333 | 55.0667 | 56.3 | 57.5333 | 58.7667 | 60 | 63 | 66 | 69 | 72 | 75 | 76.6 | 78.2 | 79.8 | 81.4 | 83
N-1 | 98755.5743 | Flex-1 | 2088.0515 | 3165.0847 | 4242.1179 | 5319.151 | 6396.1842 | 7473.2174 | 8550.2506 | 9627.2837 | 10704.3169 | 11781.3501 | 12858.3832 | 13935.4164 | 15012.4496 | 16089.4828 | 17166.5159 | 18243.5491 | 19320.5823 | 20397.6154 | 21474.6486 | 22551.6818 | 23628.7149 | 24705.7481 | 25782.7813 | 26859.8145 | 27936.8476 | 29013.8808 | 30090.914 | 31167.9471
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 625479.561 | Flex-2-2 | 43849.6441 | 47666.1912 | 51623.0473 | 54016.9826 | 56464.4711 | 58848.3085 | 61506.8809 | 64212.3112 | 66996.4044 | 69825.2804 | 72773.518 | 75714.333 | 78717.3741 | 81702.7173 | 84628.6566 | 87572.1253 | 90542.9416 | 93513.3844 | 96262.8354 | 99037.2825 | 101828.9405 | 104676.614 | 107213.1187 | 109729.1881 | 112291.2474 | 114921.1958 | 117146.0692 | 119382.045
N-0 | 10376.9204 | EENS | 49.8 | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1509.75 | 1772.8 | 2035.85 | 2539.0833 | 2701.7867 | 2864.49 | 3022.3933 | 3147.7467 | 3273.1 | 3075.0533 | 2877.0067 | 2678.96 | 2480.9133 | 1741.6 | 1294.8636 | 848.1273 | 401.3909 | -45.3455 | -2295.5
N-0 | 839.4895 | IP | 22.4 | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 146.8 | 147.55 | 148.3 | 149.4 | 147.04 | 144.68 | 142.32 | 139.96 | 107 | 93.22 | 79.44 | 65.66 | 51.88 | 38.8 | 25.7382 | 12.6764 | -0.38545 | -13.4473 | -22.2
N-0 | 601.4071 | SAIDI | 0.212 | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 52.594 | 69.1341 | 85.6743 | 139.9104 | 168.1841 | 196.4577 | 224.7314 | 253.0051 | 280.8642 | 283.8029 | 286.7417 | 289.6804 | 292.6191 | 196.4421 | 174.8276 | 153.213 | 131.5985 | 109.984 | -602.5574
N-0 | 10.5431 | SAIFI | 0.053001 | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.5361 | 1.7454 | 1.9546 | 2.4195 | 2.5964 | 2.7733 | 2.9502 | 3.1271 | 3.2349 | 2.941 | 2.6471 | 2.3533 | 2.0594 | 1.0891 | 1.015 | 0.94089 | 0.86679 | 0.7927 | 1.6525
N-0 | 121.8543 | PFD | 4 | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 24.75 | 26 | 27.25 | 29.3333 | 27.2667 | 25.2 | 23.1333 | 21.0667 | 13 | 10.3 | 7.6 | 4.9 | 2.2 | -2 | -5.2727 | -8.5455 | -11.8182 | -15.0909 | -23
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.3837 | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.6995 | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 162.5343 | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 150.0851 | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 1002742.6621 | 16.2698 | -3347.7459 | -2144.7603 | -941.7746 | 261.211 | 1464.1967 | 2667.1823 | 3870.168 | 10820.6961 | 17771.2243 | 24721.7524 | 31672.2806 | 135060.1241 | 154562.0859 | 174064.0476 | 193566.0094 | 213067.9712 | 232569.933 | 310473.2243 | 388376.5155 | 466279.8067 | 544183.098 | 622086.3892 | 752039.628 | 881992.8668 | 1011946.1056 | 1141899.3444 | 1271852.5832
Commerical(N-1) | EENS | 4160917.7071 | 67.5111 | -13889.0354 | -8894.8747 | -3900.714 | 1093.4467 | 6087.6075 | 11081.7682 | 16075.9289 | 44913.7026 | 73751.4763 | 102589.25 | 131427.0237 | 560430.0708 | 641353.1849 | 722276.299 | 803199.4132 | 884122.5273 | 965045.6414 | 1288304.2444 | 1611562.8474 | 1934821.4504 | 2258080.0534 | 2581338.6564 | 3120577.7792 | 3659816.902 | 4199056.0249 | 4738295.1477 | 5277534.2705
Aggregate | EENS | 5163660.3692 | 83.7809 | -17236.7813 | -11039.6349 | -4842.4886 | 1354.6578 | 7551.8042 | 13748.9505 | 19946.0969 | 55734.3987 | 91522.7006 | 127311.0025 | 163099.3043 | 695490.1949 | 795915.2708 | 896340.3467 | 996765.4226 | 1097190.4985 | 1197615.5744 | 1598777.4687 | 1999939.3629 | 2401101.2571 | 2802263.1513 | 3203425.0456 | 3872617.4072 | 4541809.7688 | 5211002.1305 | 5880194.4921 | 6549386.8537
Residential (N-0) | EENS | 54138723.56 | 310386.798 | 817408.1222 | 1334522.6987 | 1839795.548 | 2286697.9913 | 2696419.0539 | 3587048.7001 | 4534084.5658 | 5693348.9186 | 7427041.24 | 9237296.1549 | 11243683.5382 | 13242127.649 | 14657755.1207 | 15922439.3429 | 17341617.8686 | 17894172.7982 | 17734817.6491 | 16974626.131 | 17425482.4148 | 15680218.0025 | 13217136.9787 | 10523501.5999 | 6429366.5629 | 2952431.3424 | -996624.3672 | -6782049.1411 | -9999692.4363
Commerical(N-0) | EENS | 233897115.1718 | 1628153.2445 | 4276437.7225 | 6406619.8341 | 8961966.1784 | 10695561.9976 | 11935292.0944 | 15941642.3225 | 19613619.8153 | 24661704.485 | 32066870.8602 | 39971861.0198 | 49398898.1353 | 59065858.254 | 63722350.5725 | 67985155.9168 | 74920746.9528 | 75781588.9184 | 73155353.4041 | 69024292.3031 | 74087494.4063 | 65342374.3253 | 54719578.1537 | 43865517.1901 | 25526484.1587 | 11085387.0075 | -5050035.4563 | -31392186.7923 | -50450403.0887
Aggregate | EENS | 288035838.7318 | 1938540.0425 | 5093845.8447 | 7741142.5328 | 10801761.7264 | 12982259.9888 | 14631711.1483 | 19528691.0227 | 24147704.381 | 30355053.4036 | 39493912.1002 | 49209157.1747 | 60642581.6735 | 72307985.903 | 78380105.6932 | 83907595.2598 | 92262364.8214 | 93675761.7166 | 90890171.0532 | 85998918.4341 | 91512976.8211 | 81022592.3278 | 67936715.1324 | 54389018.79 | 31955850.7215 | 14037818.35 | -6046659.8235 | -38174235.9334 | -60450095.525
Residential (N-1) | Value for Flex-1 | 542122761.4057 | 8238114.0347 | 12799582.0479 | 17583974.6405 | 22599587.1239 | 27854990.2474 | 33359038.7851 | 39120880.3807 | 45149964.6569 | 51456052.5967 | 58049226.2056 | 64939898.462 | 72138823.5649 | 79657107.4864 | 87506218.8392 | 95698000.0675 | 104244678.9704 | 113158880.5684 | 122453639.322 | 132142411.7129 | 142239089.1988 | 152758011.5516 | 163713980.5914 | 175122274.3259 | 186998661.5092 | 199359416.6303 | 212221335.344 | 225601750.3579 | 239518547.788
Commerical(N-1) | Value for Flex-1 | 2233346554.7265 | 33938002.4352 | 52729574.3762 | 72439513.6626 | 93101993.9295 | 114752323.5136 | 137426980.8307 | 161163650.8115 | 186001262.4283 | 211980027.3442 | 239141479.7169 | 267528517.1911 | 297185443.1142 | 328158010.0103 | 360493464.3491 | 394240592.6487 | 429449768.948 | 466173003.6919 | 504463994.0674 | 544378175.8343 | 585972776.6933 | 629306871.2354 | 674441437.5191 | 721439415.3225 | 770365766.1176 | 821287534.8179 | 874273913.3493 | 929396306.0981 | 986728397.2885
Aggregate | Value for Flex-1 | 2775469316.1322 | 42176116.4699 | 65529156.424 | 90023488.3031 | 115701581.0534 | 142607313.761 | 170786019.6158 | 200284531.1923 | 231151227.0853 | 263436079.941 | 297190705.9225 | 332468415.6531 | 369324266.6791 | 407815117.4966 | 447999683.1883 | 489938592.7162 | 533694447.9184 | 579331884.2603 | 626917633.3894 | 676520587.5472 | 728211865.8921 | 782064882.787 | 838155418.1104 | 896561689.6483 | 957364427.6268 | 1020646951.4481 | 1086495248.6933 | 1154998056.4561 | 1226246945.0765
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 201421523.7425 | 11415404.7265 | 12677256.0862 | 14005928.335 | 14898443.9956 | 16001404.1511 | 17079540.6575 | 18025564.8207 | 19173409.5383 | 20408716.3778 | 21700257.5548 | 23225050.5217 | 24562337.3095 | 26000278.4294 | 27628571.2119 | 29216356.1057 | 31019684.7629 | 32721790.7961 | 34498473.5373 | 36216597.8881 | 38085174.9541 | 39829235.0504 | 41537971.8595 | 43666848.8026 | 45674640.5094 | 47592810.1302 | 49813062.131 | 52005419.7536 | 54190723.0631
Aggregate ($M) |  | 3270.0903 | 55530145.0197 | 83283021.5737 | 111759519.536 | 141396944.2868 | 171592332.5587 | 202504823.2258 | 237852535.9862 | 274492287.1015 | 314255584.1211 | 358476398.2781 | 405029934.352 | 454692284.9665 | 506818872.0239 | 554804275.3642 | 603958884.4284 | 657973262.9253 | 706826627.2716 | 753503893.5542 | 800334881.3381 | 859809957.0302 | 905317811.4223 | 950432368.2536 | 997820982.2866 | 1038867536.2649 | 1086819389.6971 | 1135472653.1313 | 1174709434.7683 | 1226536959.4683
Aggregate ($M)+ Monetized Losses |  | 3270.4391 | 55544497.0197 | 83299776.2237 | 111778498.1068 | 141418247.5028 | 171616064.7906 | 202531092.6098 | 237881454.5473 | 274523970.8802 | 314290153.3042 | 358513977.3334 | 405070652.1674 | 454736274.9931 | 506866272.4236 | 554855229.1619 | 604013539.6687 | 658031772.8343 | 706889150.4232 | 753570594.0419 | 800405928.9516 | 859885527.4379 | 905398086.3594 | 950517535.715 | 997911236.7265 | 1038963078.8027 | 1086920428.3287 | 1135579402.9473 | 1174822118.1787 | 1226655806.4343
Project Cost |  | 185
Benefit-Cost Ratio |  | 17.678

## 15 - Distributed Storage-10%-4H (hidden)
10% Distributed Storage
| Equipment Categories All costs are $x1,000 | [6 empty] | Units | kV | Cost | Adjusted Cost
1 | New Substation Equipment
| 500kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 36194.3937 | 0 |  | 0
| 115kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 4403.9172 | 1 |  | 4403.9172
| 230kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 17710.3457 | 0 |  | 0
2 | Transformer Banks
| 500/115 kV 1-3 Phase |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 24748.4568 | 0 |  | 0
| 230/115 kV |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 8756.8817 | 1 |  | 8756.8817
kV
3 | Line Positions to terminate ties and Transformer Bank positions |  |  |  | 230 | 500 | 115
| Single Breaker (add third breaker to breaker and a half) |  |  |  | 2145.4637 | 5398.3718 | 1437.1815 | 0 | 115 | 0
| Breaker and a half (2CB) |  |  |  | 3607.9737 | 8587.7771 | 2149.8636 | 0 | 230 | 0
| Breaker and a half (3CB) |  |  |  | 5291.2883 | 12131.4222 | 3436.5983 | 1 | 115 | 3436.5983
| Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | Used in substation expansion |  | 540.3386 |  | 252.4804 | 0 | 115 | 0
4 | Shunt Capacitors | [5 empty] | 2006.8433 | 0 |  | 0
5 | Fiber optic cable on existing poles | /mile |  |  |  | 99 | 99 | 0 |  | 0
| Fiber optic cable on new poles | /mile |  |  |  | 134 | 134 | 0
6 | Single Circuit, Lattice Tower | /mile |  |  | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
[5 empty] | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
| Double Circuit, Strung on both sides, Lattice Tower | /mile |  |  | 4494.8333 | 9381.7495 | 2174.744
| Rebuild/reconductor existing single circuit line section - Metropolitan | /mile |  |  |  |  | 1381.7727 | 0 |  | 0
| Rebuild/reconductor existing double circuit line section - Metropolitan | /mile |  |  |  |  | 1454.8259 | 0 |  | 0
7 | Disconnect switches (incl. steel structures and foundations) |  |  |  | 3326.9104 | 19935.5969 | 105.461 | 0 | 115 | 0 |  | T&D Costs | 16597.3971
8 | Energy Storage |  |  |  |  | Base price
2024 | Battery Price (Power) | $/kW |  |  |  | 175 | #REF! | 122.896 |  | #REF! | #REF!
2024 | Battery Price (Energy) | $/kWh |  |  |  | 350 | #REF! | 245.792 |  | #REF!
2024 | Battery Price (Energy uprate) | $/kWh |  |  |  | 350 | #REF! | 282.3378 |  | #REF! | #REF!
[12 empty] | ESS-1 | #REF!
2030 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 7.1307 |  | #REF! | #REF!
2030 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 14.2615 |  | #REF!
2030 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 51.9828 |  | #REF! | #REF!
[12 empty] | ESS-2 | #REF!
[12 empty] | ESS-2 W escalation | #REF!
2035 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 7.5856 |  | #REF! | #REF!
2035 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 15.1713 |  | #REF!
2035 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 54.1432 |  | #REF! | #REF!
2035 | Inverter Replacement | $/kW | [5 empty] | 116.1909 |  | #REF! |  | ESS-3 | #REF!
[12 empty] | ESS-3 W escalation | #REF!
2040 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 8.072 |  | #REF! | #REF!
2040 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 16.144 |  | #REF!
2040 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 56.4467 |  | #REF! | #REF!
2040 | Inverter Replacement | MW | [5 empty] | 13.8358 |  | #REF! |  | ESS-4 | #REF!
2040 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF! |  | ESS-4 W escalation | #REF!
2045 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 5.0906 |  | #REF! | #REF!
2045 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 10.1812 |  | #REF!
2045 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 51.1071 |  | #REF! | #REF!
2045 | Inverter Replacement | MW | [5 empty] | 7.5856 |  | #REF!
2045 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF!
[12 empty] | ESS-5 | #REF!
[12 empty] | ESS-5 w escalation | #REF!
| Total Cost | [8 empty] | 196711.6307
| Total Cost with Contingency | [8 empty] | #REF!
| Total Cost with SCE Escalation Rate | [8 empty] | #REF!
Factor Amounts: |  |  |  |  | Low Impact factors: |  |  | Medium Impact factors: |  |  | High Impact factors:
| Terrain (CAISO per unit costs) |  |  |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  |  | 2.0X to 3.0X
| Terrain (User specified) |  |  |  |  | 1.25 |  |  | 1.5 |  |  | 2
| Population density (CAISO per unit costs) |  |  |  |  | 1.00X to 1.10X |  |  | 1.33X |  |  | 1.67X
| Population density(User specified) |  |  |  |  | 1.1 |  |  | 1.33 |  |  | 1.67
| Weather study (CAISO per unit costs) |  |  |  |  | 1.35X |  |  | 1.45X |  |  | 1.60X
| Weather study(User specified) |  |  |  |  | 1.35 |  |  | 1.45 |  |  | 1.6
| Factor Type |  |  | Explanation of Factor issues and Factor multipliers
| Terrain |  |  | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
| Population density |  |  | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
| Weather study |  |  | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
[5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2030 and beyond
|  |  |  | Escalation Rate | 2.696% | 2.138% | 2.556% | 2.352% | 2.287% | 2.333% | 2.249% | 2.332% | 2.295% | 2.01% | 2.212% | 0.023
|  |  |  | Escalation Factors | 1 | 1.0214 | 1.0475 | 1.0721 | 1.0966 | 1.1222 | 1.1475 | 1.1742 | 1.2012 | 1.2253 | 1.2524 | 1.2812
| Contingency Factor |  | #REF!
| Contingency Factor for battery | Power | #REF!
|  | Energy | #REF!
Notes
| Contingency Factor included to account for the following considerations |  |  |  | 2018: The SDGE project has been ranked as high impact due to terrain and population, primarily driven by the complications associated with traversing the Pechanga Reservation
o Review of customer/developer existing and proposed plans (i.e. surveyed base map, street/land
improvements, profiles, grading, overhead & underground utilities, temp construction roads &
laydown/staging yards, etc.)
o Property rights study
o Right-of-way improvements/acquisitions (i.e. easements, access/maintenance roads, grading, etc.)
o GO 131-D engineering/permitting per CEQA requirements
o Non-GO 131-D Permitting (i.e. Railroad, City, County, State, Federal Agency, etc.)
o Governing regulation impacts (i.e. CPUC, FERC, OSHA, etc.)
o Environmental study and mitigations
o EMF study and potential reduction mitigations as required by the CPUC
o Geotechnical investigation and mitigations
o Surveys
o Potholing
o Traffic plans/control
o Concrete and/or asphalt repairs
o Associated SCE Substation work (i.e. breaker replacements, switch-rack position relocations, etc.)
o Associated SCE Distribution voltage under-build work (i.e. 16 kV, 12 kV, 4 kV, and secondary
conductors)
o Associated SCE Telecommunication under-build work
o Associated 3rd Party Joint Owners and renters/tenants under-build work (i.e. cable TV,
communication cable, fiber optic, etc.)
o Conflicts associated with other projects in the same geographical area or electrical system
o Availability of line outages required for construction
Unit costs exclude Licensing.
| ESS O&M | #REF! | $/kWh
| + | 1% | of EPC Cost |  | 2020: Add contingency for battery value
| Price Escalation | 2.5% |  |  | 2020: Battery cost reduction = 0%, global factor, and what it changes
| T&D Annual OPEX | #REF! |  |  | 2020: Include 2% into battery price escalation
| Inverter Replacement Cost | #REF! | $/kWh |  | 2020: Make the significant digits, 1000$ of dollars
| Battery Replacement Cost | #REF! | % Capex |  | 2020: shift it to 99 instead of 90, not take actual MW
| Annual Battery Cost Change | #REF!
| Price Stabizes in | #REF!
| Calendar Time (Year) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| O&M T&D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Initial CapEx costs | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental costs | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| MW | 112.3607 | 1.2611 | 1.2767 | 1.2924 | 1.3083 | 1.3244 | 1.3408 | 1.3574 | 1.3742 | 1.3912 | 1.4084 | 1.4259 | 1.4436 | 1.4616 | 1.4798 | 1.4982 | 1.5169 | 1.5358 | 1.555 | 1.5744 | 1.5942 | 1.6141 | 1.6344 | 1.6549 | 1.6757 | 1.6968 | 1.7181
| MWh | 449.4429 | 5.0446 | 5.1066 | 5.1695 | 5.2332 | 5.2978 | 5.3632 | 5.4295 | 5.4967 | 5.5648 | 5.6337 | 5.7036 | 5.7745 | 5.8463 | 5.919 | 5.9928 | 6.0675 | 6.1432 | 6.22 | 6.2978 | 6.3766 | 6.4565 | 6.5375 | 6.6196 | 6.7028 | 6.7871 | 6.8725
| MWh uprate | 458.4317 | 14.1343 | 14.2985 | 14.4648 | 14.6332 | 14.8037 | 14.9764 | 15.1513 | 15.3284 | 15.5077 | 15.6894 | 15.8734 | 16.0597 | 16.2484 | 16.4396 | 16.6332 | 16.8292 | 17.0278 | 17.229 | 17.4327 | 17.6391 | 17.8481 | 18.0599 | 18.2743 | 18.4916 | 18.7116 | 18.9345
| Battery price | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902
| Energy price | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804
| Inverter replacement MW | [10 empty] | 112.3607 | 1.2611 | 1.2767 | 1.2924 | 1.3083 | 1.3244 | 1.3408 | 1.3574 | 1.3742 | 1.3912 | 1.4084 | 1.4259 | 1.4436 | 1.4616 | 1.4798 | 1.4982 | 1.5169
| Battery costs | 180114.2336 | 5167.72 | 5227.8994 | 5288.8435 | 5350.5628 | 5413.0679 | 5476.3696 | 5540.4788 | 4570.4956 | 4624.1126 | 4678.4156 | 4733.414 | 4789.1174 | 4845.5354 | 4902.6781 | 4960.5554 | 5019.1774 | 5078.5545 | 5138.6971 | 5199.6159 | 5261.3216 | 5323.8251 | 5387.1376 | 5451.2703 | 5516.2347 | 5582.0422 | 5648.7048
| Inverter replacement costs | [10 empty] | 16032.776 | 179.9535 | 182.167 | 184.4099 | 186.6827 | 188.9858 | 191.3195 | 193.6843 | 196.0807 | 198.5091 | 200.9699 | 203.4637 | 205.9909 | 208.552 | 211.1475 | 213.7778 | 216.4435
| Initial CapEx costs | #REF! 2022: #REF!
| Battery replacement costs | #REF! 2042: 90057.1168; #REF! 2043: 2583.86; #REF! 2044: 2613.9497; #REF! 2045: 2644.4217; #REF! 2046: 2675.2814; #REF! 2047: 2706.5339; #REF! 2048: 2738.1848
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!

## 15 - Cost Benefit (hidden)
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-1 |  | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 |  | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 |  | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 10% Distributed Energy Storage | Losses (MWh) | 38659.7 | 39104.55 | 39252.8333 | 39104.55 | 39703.4761 | 40302.4022 | 40901.3283 | 41500.2543 | 42099.1804 | 42698.1065 | 43297.0326 | 43895.9587 | 44494.8848 | 45093.8109 | 45692.737 | 46291.663 | 46890.5891 | 47489.5152 | 48088.4413 | 48687.3674 | 49286.2935 | 49885.2196 | 50484.1457 | 51083.0717 | 51681.9978 | 52280.9239 | 52879.85
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 138.6549 | 256.1959 | 373.737 | 491.278 | 608.8191 | 726.3602 | 1059.3293 | 1392.2984 | 1725.2676 | 2058.2367 | 2391.2058 | 3025.2803 | 3659.3548 | 4293.4293
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 4.2734 | 5.9245 | 7.5756 | 9.2267 | 10.8778 | 12.5289 | 16.598 | 20.6671 | 24.7363 | 28.8054 | 32.8745 | 41.8131 | 50.7517 | 59.6904
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 9.8622 | 23.7273 | 37.5924 | 51.4574 | 65.3225 | 79.1876 | 148.2636 | 217.3397 | 286.4157 | 355.4918 | 424.5678 | 582.7717 | 740.9757 | 899.1796
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 0.12349 | 0.22207 | 0.32065 | 0.41923 | 0.51781 | 0.61639 | 0.92915 | 1.2419 | 1.5547 | 1.8674 | 2.1802 | 2.7625 | 3.3449 | 3.9273
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 10.3959 | 14.8166 | 19.2372 | 23.6579 | 28.0786 | 32.4993 | 41.8294 | 51.1596 | 60.4898 | 69.8199 | 79.1501 | 93.2111 | 107.2722 | 121.3332
N-1 |  | Available Flex-1 | 8.07 | 93.5288 | 178.9877 | 264.4465 | 349.9054 | 435.3642 | 520.8231 | 606.2819 | 691.7408 | 777.1996 | 862.6585 | 948.1173 | 1033.5762 | 1119.035 | 1204.4938 | 1289.9527 | 1375.4115 | 1460.8704 | 1546.3292 | 1631.7881 | 1717.2469 | 1802.7058 | 1888.1646 | 1973.6235 | 2059.0823 | 2144.5412 | 2230
N-1 |  | Available Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 354.12 | 566.5409 | 778.9619 | 991.3828 | 1203.8038 | 1416.2247 | 1952.5059 | 2488.787 | 3025.0682 | 3561.3494 | 4097.6305 | 4982.1362 | 5866.6418 | 6751.1474
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 124.34 | 140.54 | 156.74 | 172.94 | 189.14 | 205.34 | 230.5458 | 255.7516 | 280.9575 | 306.1633 | 331.3691 | 348.274 | 365.1789 | 382.0837
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 2.58 | 7.238 | 11.896 | 16.554 | 21.212 | 25.87 | 55.13 | 84.39 | 113.65 | 142.91 | 172.17 | 238.1175 | 304.065 | 370.0125
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 0.3234 | 0.51672 | 0.71004 | 0.90336 | 1.0967 | 1.29 | 1.78 | 2.27 | 2.76 | 3.25 | 3.74 | 4.549 | 5.3579 | 6.1669
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  |  |  | 8 | 10.4 | 12.8 | 15.2 | 17.6 | 20 | 25.2 | 30.4 | 35.6 | 40.8 | 46 | 50.6667 | 55.3333 | 60
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 122489.8233 | Losses (MWh) | 12228.35 | 12380.0038 | 12828.2244 | 13573.0115 | 13570.5893 | 13568.1671 | 13565.7448 | 13563.3226 | 13560.9003 | 13558.4781 | 13556.0559 | 13553.6336 | 13551.2114 | 13548.7891 | 13546.3669 | 13543.9446 | 13541.5224 | 13539.1002 | 13536.6779 | 13534.2557 | 13531.8334 | 13529.4112 | 13526.989 | 13524.5667 | 13522.1445 | 13519.7222 | 13517.3
| 6043531.5976 | Losses ($) | 489134 | 507580.1577 | 539106.1287 | 584665.9552 | 599175.656 | 614045.4257 | 629284.1991 | 644901.1327 | 660905.6104 | 677307.2488 | 694115.9031 | 711341.6731 | 728994.9091 | 747086.2184 | 765626.4714 | 784626.8081 | 804098.6451 | 824053.6822 | 844503.9095 | 865461.6146 | 886939.39 | 908950.1407 | 931507.0918 | 954623.7966 | 978314.1447 | 1002592.3704 | 1027473.061
N-1 | 8152.38 | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1428.4951 | 1600.2041 | 1771.913 | 1943.622 | 2506.1509 | 3068.6798 | 3415.7807 | 3762.8816 | 3537.4324 | 3999.0433 | 4460.6542 | 4621.1597 | 4781.6652 | 4942.1707
N-1 | 251.4877 | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 44.0266 | 46.7755 | 49.5244 | 52.2733 | 52.6022 | 52.9311 | 50.842 | 48.7529 | 46.6637 | 53.9946 | 61.3255 | 63.7869 | 66.2483 | 68.7096
N-1 | 845.9274 | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 101.6055 | 116.4059 | 131.2062 | 146.0066 | 240.2766 | 334.5466 | 373.6057 | 412.6648 | 451.7238 | 621.8651 | 792.0064 | 873.0197 | 954.0331 | 1035.0465
N-1 | 7.1507 | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.2723 | 1.4354 | 1.5985 | 1.7616 | 2.1829 | 2.6041 | 2.8112 | 3.0182 | 3.2253 | 3.6462 | 4.067 | 4.2182 | 4.3695 | 4.5207
N-1 | 667.2384 | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 107.1041 | 112.5168 | 117.9294 | 123.3421 | 130.3214 | 137.3007 | 139.3706 | 141.4404 | 143.5102 | 145.5801 | 147.6499 | 144.9889 | 142.3278 | 139.6668
N-1 | #REF! | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 | #REF! | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 | 18930.8368 | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 3648.33 | 4015.2924 | 4382.2548 | 4749.2172 | 5366.1962 | 5983.1753 | 6276.2941 | 6569.413 | 6862.5318 | 7253.2106 | 7643.8895 | 7686.3438 | 7728.7982 | 7771.2526
N-0 | 981.4592 | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 110.66 | 109.46 | 108.26 | 107.06 | 104.54 | 102.02 | 90.4942 | 78.9684 | 67.4425 | 54.6767 | 41.9109 | 37.446 | 32.9811 | 28.5163
N-0 | 1856.4602 | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 247.3609 | 300.36 | 353.3592 | 406.3583 | 534.3171 | 662.276 | 787.4348 | 912.5936 | 1037.7524 | 1256.8248 | 1475.8972 | 1695.503 | 1915.1087 | 1824.702
N-0 | 20.8037 | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 3.9363 | 4.3596 | 4.7829 | 5.2062 | 5.8956 | 6.5849 | 6.9777 | 7.3704 | 7.7631 | 8.2596 | 8.7561 | 8.9337 | 9.1113 | 9.2889
N-0 | 256.6362 | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 45 | 47.9333 | 50.8667 | 53.8 | 58 | 62.2 | 63.6 | 65 | 66.4 | 69.2 | 72 | 75.3333 | 78.6667 | 82
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Project Cost |  | #REF!
Benefit-Cost Ratio |  | #REF!

## 16 - Distributed Storage-30%-4H (hidden)
10% Distributed Storage
| Equipment Categories All costs are $x1,000 | [6 empty] | Units | kV | Cost | Adjusted Cost
1 | New Substation Equipment
| 500kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 36194.3937 | 0 |  | 0
| 115kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 4403.9172 | 1 |  | 4403.9172
| 230kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 17710.3457 | 0 |  | 0
2 | Transformer Banks
| 500/115 kV 1-3 Phase |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 24748.4568 | 0 |  | 0
| 230/115 kV |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 8756.8817 | 1 |  | 8756.8817
kV
3 | Line Positions to terminate ties and Transformer Bank positions |  |  |  | 230 | 500 | 115
| Single Breaker (add third breaker to breaker and a half) |  |  |  | 2145.4637 | 5398.3718 | 1437.1815 | 0 | 115 | 0
| Breaker and a half (2CB) |  |  |  | 3607.9737 | 8587.7771 | 2149.8636 | 0 | 230 | 0
| Breaker and a half (3CB) |  |  |  | 5291.2883 | 12131.4222 | 3436.5983 | 1 | 115 | 3436.5983
| Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | Used in substation expansion |  | 540.3386 |  | 252.4804 | 0 | 115 | 0
4 | Shunt Capacitors | [5 empty] | 2006.8433 | 0 |  | 0
5 | Fiber optic cable on existing poles | /mile |  |  |  | 99 | 99 | 0 |  | 0
| Fiber optic cable on new poles | /mile |  |  |  | 134 | 134 | 0
6 | Single Circuit, Lattice Tower | /mile |  |  | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
[5 empty] | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
| Double Circuit, Strung on both sides, Lattice Tower | /mile |  |  | 4494.8333 | 9381.7495 | 2174.744
| Rebuild/reconductor existing single circuit line section - Metropolitan | /mile |  |  |  |  | 1381.7727 | 0 |  | 0
| Rebuild/reconductor existing double circuit line section - Metropolitan | /mile |  |  |  |  | 1454.8259 | 0 |  | 0
7 | Disconnect switches (incl. steel structures and foundations) |  |  |  | 3326.9104 | 19935.5969 | 105.461 | 0 | 115 | 0 |  | T&D Costs | 16597.3971
8 | Energy Storage |  |  |  |  | Base price
2024 | Battery Price (Power) | $/kW |  |  |  | 175 | #REF! | 337.0822 |  | #REF!
2024 | Battery Price (Energy) | $/kWh |  |  |  | 310 | #REF! | 674.1643 |  | #REF!
2024 | Battery Price (Energy uprate) | $/kWh |  |  |  | 310 | #REF! | 789.8909 |  | #REF!
[12 empty] | ESS-1 | #REF!
2030 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 21.3922 |  | #REF!
2030 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 42.7844 |  | #REF!
2030 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 162.9641 |  | #REF!
[12 empty] | ESS-2 | #REF!
[12 empty] | ESS-2 W escalation | #REF!
2035 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 22.7569 |  | #REF!
2035 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 45.5138 |  | #REF!
2035 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 170.4306 |  | #REF!
2035 | Inverter Replacement | $/kW | [5 empty] | 368.688 |  | #REF! |  | ESS-3 | #REF!
[12 empty] | ESS-3 W escalation | #REF!
2040 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 24.216 |  | #REF!
2040 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 48.4319 |  | #REF!
2040 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 178.3896 |  | #REF!
2040 | Inverter Replacement | MW | [5 empty] | 21.3922 |  | #REF! |  | ESS-4 | #REF!
2040 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF! |  | ESS-4 W escalation | #REF!
2045 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 15.2718 |  | #REF!
2045 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 30.5435 |  | #REF!
2045 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 163.6802 |  | #REF!
2045 | Inverter Replacement | MW | [5 empty] | 22.7569 |  | #REF!
2045 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF!
[12 empty] | ESS-5 | #REF!
[12 empty] | ESS-5 w escalation | #REF!
| Total Cost | [8 empty] | 556940.098
| Total Cost with Contingency | [8 empty] | #REF!
| Total Cost with SCE Escalation Rate | [8 empty] | #REF!
Factor Amounts: |  |  |  |  | Low Impact factors: |  |  | Medium Impact factors: |  |  | High Impact factors:
| Terrain (CAISO per unit costs) |  |  |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  |  | 2.0X to 3.0X
| Terrain (User specified) |  |  |  |  | 1.25 |  |  | 1.5 |  |  | 2
| Population density (CAISO per unit costs) |  |  |  |  | 1.00X to 1.10X |  |  | 1.33X |  |  | 1.67X
| Population density(User specified) |  |  |  |  | 1.1 |  |  | 1.33 |  |  | 1.67
| Weather study (CAISO per unit costs) |  |  |  |  | 1.35X |  |  | 1.45X |  |  | 1.60X
| Weather study(User specified) |  |  |  |  | 1.35 |  |  | 1.45 |  |  | 1.6
| Factor Type |  |  | Explanation of Factor issues and Factor multipliers
| Terrain |  |  | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
| Population density |  |  | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
| Weather study |  |  | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
[5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2030 and beyond
|  |  |  | Escalation Rate | 2.696% | 2.138% | 2.556% | 2.352% | 2.287% | 2.333% | 2.249% | 2.332% | 2.295% | 2.01% | 2.212% | 0.023
|  |  |  | Escalation Factors | 1 | 1.0214 | 1.0475 | 1.0721 | 1.0966 | 1.1222 | 1.1475 | 1.1742 | 1.2012 | 1.2253 | 1.2524 | 1.2812
| Contingency Factor |  | #REF!
| Contingency Factor for battery | Power | #REF!
|  | Energy | #REF!
Notes
| Contingency Factor included to account for the following considerations |  |  |  | 2018: The SDGE project has been ranked as high impact due to terrain and population, primarily driven by the complications associated with traversing the Pechanga Reservation
o Review of customer/developer existing and proposed plans (i.e. surveyed base map, street/land
improvements, profiles, grading, overhead & underground utilities, temp construction roads &
laydown/staging yards, etc.)
o Property rights study
o Right-of-way improvements/acquisitions (i.e. easements, access/maintenance roads, grading, etc.)
o GO 131-D engineering/permitting per CEQA requirements
o Non-GO 131-D Permitting (i.e. Railroad, City, County, State, Federal Agency, etc.)
o Governing regulation impacts (i.e. CPUC, FERC, OSHA, etc.)
o Environmental study and mitigations
o EMF study and potential reduction mitigations as required by the CPUC
o Geotechnical investigation and mitigations
o Surveys
o Potholing
o Traffic plans/control
o Concrete and/or asphalt repairs
o Associated SCE Substation work (i.e. breaker replacements, switch-rack position relocations, etc.)
o Associated SCE Distribution voltage under-build work (i.e. 16 kV, 12 kV, 4 kV, and secondary
conductors)
o Associated SCE Telecommunication under-build work
o Associated 3rd Party Joint Owners and renters/tenants under-build work (i.e. cable TV,
communication cable, fiber optic, etc.)
o Conflicts associated with other projects in the same geographical area or electrical system
o Availability of line outages required for construction
Unit costs exclude Licensing.
| ESS O&M | #REF! | $/kWh
| + | 1% | of EPC Cost |  | 2020: Add contingency for battery value
| Price Escalation | 2.5% |  |  | 2020: Battery cost reduction = 0%, global factor, and what it changes
| T&D Annual OPEX | #REF! |  |  | 2020: Include 2% into battery price escalation
| Inverter Replacement Cost | #REF! | $/kWh |  | 2020: Make the significant digits, 1000$ of dollars
| Battery Replacement Cost | #REF! | % Capex |  | 2020: shift it to 99 instead of 90, not take actual MW
| Annual Battery Cost Change | #REF!
| Price Stabizes in | #REF!
| Calendar Time (Year) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| O&M T&D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Initial CapEx costs | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| Total Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| MW | 337.0822 | 3.7834 | 3.83 | 3.8771 | 3.9249 | 3.9733 | 4.0224 | 4.0721 | 4.1225 | 4.1736 | 4.2253 | 4.2777 | 4.3309 | 4.3847 | 4.4393 | 4.4946 | 4.5506 | 4.6074 | 4.665 | 4.7233 | 4.7825 | 4.8424 | 4.9031 | 4.9647 | 5.0271 | 5.0903 | 5.1544
| MWh | 1348.3286 | 15.1338 | 15.3199 | 15.5086 | 15.6997 | 15.8934 | 16.0896 | 16.2885 | 16.49 | 16.6943 | 16.9012 | 17.1109 | 17.3235 | 17.5389 | 17.7571 | 17.9783 | 18.2025 | 18.4297 | 18.66 | 18.8933 | 19.1298 | 19.3695 | 19.6125 | 19.8587 | 20.1083 | 20.3612 | 20.6176
| MWh uprate | 1375.2952 | 42.403 | 42.8956 | 43.3944 | 43.8995 | 44.4111 | 44.9291 | 45.4538 | 45.9851 | 46.5232 | 47.0682 | 47.6201 | 48.1791 | 48.7453 | 49.3187 | 49.8995 | 50.4877 | 51.0835 | 51.6869 | 52.2982 | 52.9173 | 53.5444 | 54.1796 | 54.823 | 55.4747 | 56.1349 | 56.8036
| Battery price | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902
| Energy price | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804
| Inverter replacement MW | [10 empty] | 337.0822 | 3.7834 | 3.83 | 3.8771 | 3.9249 | 3.9733 | 4.0224 | 4.0721 | 4.1225 | 4.1736 | 4.2253 | 4.2777 | 4.3309 | 4.3847 | 4.4393 | 4.4946 | 4.5506
| Battery costs | 540342.7009 | 15503.16 | 15683.6981 | 15866.5304 | 16051.6883 | 16239.2037 | 16429.1088 | 16621.4365 | 13711.4867 | 13872.3378 | 14035.2468 | 14200.2419 | 14367.3521 | 14536.6063 | 14708.0344 | 14881.6662 | 15057.5322 | 15235.6635 | 15416.0913 | 15598.8476 | 15783.9647 | 15971.4753 | 16161.4128 | 16353.8109 | 16548.704 | 16746.1267 | 16946.1145
| Inverter replacement costs | [10 empty] | 48098.3281 | 539.8604 | 546.501 | 553.2298 | 560.0482 | 566.9573 | 573.9584 | 581.0529 | 588.242 | 595.5272 | 602.9098 | 610.3912 | 617.9728 | 625.6561 | 633.4424 | 641.3334 | 649.3304
| Initial CapEx costs | #REF! 2022: #REF!
| Battery replacement costs | #REF! 2042: 270171.3504; #REF! 2043: 7751.58; #REF! 2044: 7841.8491; #REF! 2045: 7933.2652; #REF! 2046: 8025.8442; #REF! 2047: 8119.6018; #REF! 2048: 8214.5544
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!

## 16 -Cost Benefit (hidden)
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-1 |  | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 |  | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 |  | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 30% Distributed Energy Storage | Losses (MWh) | 38659.7 | 39104.55 | 39252.8333 | 39104.55 | 39703.4761 | 40302.4022 | 40901.3283 | 41500.2543 | 42099.1804 | 42698.1065 | 43297.0326 | 43895.9587 | 44494.8848 | 45093.8109 | 45692.737 | 46291.663 | 46890.5891 | 47489.5152 | 48088.4413 | 48687.3674 | 49286.2935 | 49885.2196 | 50484.1457 | 51083.0717 | 51681.9978 | 52280.9239 | 52879.85
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 73.1023 | 214.8673 | 356.6322 | 498.3972
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 1.005 | 2.9797 | 4.9544 | 6.9291
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 12.9796 | 43.4464 | 73.9133 | 104.3801
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.066651 | 0.1964 | 0.32615 | 0.45589
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 2.4197 | 6.3081 | 10.1964 | 14.0848
N-1 |  | Available Flex-1 | 8.07 | 369.066 | 730.0619 | 1091.0579 | 1452.0539 | 1813.0498 | 2174.0458 | 2535.0418 | 2896.0377 | 3257.0337 | 3618.0297 | 3979.0256 | 4340.0216 | 4701.0176 | 5062.0135 | 5423.0095 | 5784.0055 | 6145.0014 | 6505.9974 | 6866.9934 | 7227.9893 | 7588.9853 | 7949.9813 | 8310.9773 | 8671.9732 | 9032.9692 | 9393.9652
N-1 |  | Available Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 125.27 | 344.7461 | 564.2222 | 783.6983
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 88.3155 | 134.4061 | 180.4966 | 226.5872
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.22886 | 1.5843 | 2.9398 | 4.2952
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0.11443 | 0.31491 | 0.51539 | 0.71587
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 2 | 3.3333 | 4.6667 | 6
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component |  |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 122489.8233 | Losses (MWh) | 12228.35 | 12380.0038 | 12828.2244 | 13573.0115 | 13570.5893 | 13568.1671 | 13565.7448 | 13563.3226 | 13560.9003 | 13558.4781 | 13556.0559 | 13553.6336 | 13551.2114 | 13548.7891 | 13546.3669 | 13543.9446 | 13541.5224 | 13539.1002 | 13536.6779 | 13534.2557 | 13531.8334 | 13529.4112 | 13526.989 | 13524.5667 | 13522.1445 | 13519.7222 | 13517.3
| 6043531.5976 | Losses ($) | 489134 | 507580.1577 | 539106.1287 | 584665.9552 | 599175.656 | 614045.4257 | 629284.1991 | 644901.1327 | 660905.6104 | 677307.2488 | 694115.9031 | 711341.6731 | 728994.9091 | 747086.2184 | 765626.4714 | 784626.8081 | 804098.6451 | 824053.6822 | 844503.9095 | 865461.6146 | 886939.39 | 908950.1407 | 931507.0918 | 954623.7966 | 978314.1447 | 1002592.3704 | 1027473.061
N-1 | 10505.7596 | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6778.7577 | 7431.5727 | 8084.3878 | 8737.2028
N-1 | 287.713 | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 93.195 | 102.6203 | 112.0456 | 121.4709
N-1 | 1231.7162 | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1203.5946 | 1412.345 | 1621.0955 | 1829.846
N-1 | 9.258 | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.1805 | 6.7844 | 7.3882 | 7.9921
N-1 | 753.2501 | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 224.3803 | 231.8919 | 239.4036 | 246.9152
N-1 | #REF! | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 | #REF! | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 | 23100.7316 | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11616.25 | 12323.7339 | 13031.2178 | 13738.7017
N-0 | 1393.073 | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 284.9645 | 251.3139 | 217.6634 | 184.0128
N-0 | 1931.5379 | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.6684 | 1744.5853 | 1967.5023 | 2190.4192
N-0 | 24.6083 | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.3817 | 13.1678 | 13.9538 | 14.7399
N-0 | 307.4507 | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 116 | 122.6667 | 129.3333 | 136
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Project Cost |  | #REF!
Benefit-Cost Ratio |  | #REF!

## 17 - Distributed Storage-50%-4H (hidden)
10% Distributed Storage
| Equipment Categories All costs are $x1,000 | [6 empty] | Units | kV | Cost | Adjusted Cost
1 | New Substation Equipment
| 500kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 36194.3937 | 0 |  | 0
| 115kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 4403.9172 | 1 |  | 4403.9172
| 230kV |  | Complete Loop-in Substation, equipped with one line position to terminate a single tie |  |  |  | 17710.3457 | 0 |  | 0
2 | Transformer Banks
| 500/115 kV 1-3 Phase |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 24748.4568 | 0 |  | 0
| 230/115 kV |  | Unit cost of transformer banks reflects cost of the highest MVA rated transformer for the given voltage. |  |  |  | 8756.8817 | 1 |  | 8756.8817
kV
3 | Line Positions to terminate ties and Transformer Bank positions |  |  |  | 230 | 500 | 115
| Single Breaker (add third breaker to breaker and a half) |  |  |  | 2145.4637 | 5398.3718 | 1437.1815 | 0 | 115 | 0
| Breaker and a half (2CB) |  |  |  | 3607.9737 | 8587.7771 | 2149.8636 | 0 | 230 | 0
| Breaker and a half (3CB) |  |  |  | 5291.2883 | 12131.4222 | 3436.5983 | 1 | 115 | 3436.5983
| Double Operating Bus Sections - 2 bus extensions, spanning 4 positions |  | Used in substation expansion |  | 540.3386 |  | 252.4804 | 0 | 115 | 0
4 | Shunt Capacitors | [5 empty] | 2006.8433 | 0 |  | 0
5 | Fiber optic cable on existing poles | /mile |  |  |  | 99 | 99 | 0 |  | 0
| Fiber optic cable on new poles | /mile |  |  |  | 134 | 134 | 0
6 | Single Circuit, Lattice Tower | /mile |  |  | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
[5 empty] | 2897.3658 | 4578.5833 | 1815.3927 | 0 | 115 | 0 | 0
| Double Circuit, Strung on both sides, Lattice Tower | /mile |  |  | 4494.8333 | 9381.7495 | 2174.744
| Rebuild/reconductor existing single circuit line section - Metropolitan | /mile |  |  |  |  | 1381.7727 | 0 |  | 0
| Rebuild/reconductor existing double circuit line section - Metropolitan | /mile |  |  |  |  | 1454.8259 | 0 |  | 0
7 | Disconnect switches (incl. steel structures and foundations) |  |  |  | 3326.9104 | 19935.5969 | 105.461 | 0 | 115 | 0 |  | T&D Costs | 16597.3971
8 | Energy Storage |  |  |  |  | Base price
2024 | Battery Price (Power) | $/kW |  |  |  | 175 | #REF! | 614.4801 |  | #REF!
2024 | Battery Price (Energy) | $/kWh |  |  |  | 310 | #REF! | 1228.9601 |  | #REF!
2024 | Battery Price (Energy uprate) | $/kWh |  |  |  | 310 | #REF! | 1439.9227 |  | #REF!
[12 empty] | ESS-1 | #REF!
2030 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 35.6537 |  | #REF!
2030 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 71.3073 |  | #REF!
2030 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 289.6916 |  | #REF!
[12 empty] | ESS-2 | #REF!
[12 empty] | ESS-2 W escalation | #REF!
2035 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 37.9282 |  | #REF!
2035 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 75.8564 |  | #REF!
2035 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 302.1359 |  | #REF!
2035 | Inverter Replacement | $/kW | [5 empty] | 614.4801 |  | #REF! |  | ESS-3 | #REF!
[12 empty] | ESS-3 W escalation | #REF!
2040 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 40.36 |  | #REF!
2040 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 80.7199 |  | #REF!
2040 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 315.4008 |  | #REF!
2040 | Inverter Replacement | MW | [5 empty] | 35.6537 |  | #REF! |  | ESS-4 | #REF!
2040 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF! |  | ESS-4 W escalation | #REF!
2045 | Battery Price (Power) | $/kW |  |  |  | #REF! | #REF! | 25.4529 |  | #REF!
2045 | Battery Price (Energy) | $/kWh |  |  |  | #REF! | #REF! | 50.9059 |  | #REF!
2045 | Battery Price (Energy uprate) | $/kWh |  |  |  | #REF! | #REF! | 290.8851 |  | #REF!
2045 | Inverter Replacement | MW | [5 empty] | 37.9282 |  | #REF!
2045 | Battery Replacement | Cost in $ | [5 empty] | #REF! |  | #REF!
[12 empty] | ESS-5 | #REF!
[12 empty] | ESS-5 w escalation | #REF!
| Total Cost | [8 empty] | 917168.5652
| Total Cost with Contingency | [8 empty] | #REF!
| Total Cost with SCE Escalation Rate | [8 empty] | #REF!
Factor Amounts: |  |  |  |  | Low Impact factors: |  |  | Medium Impact factors: |  |  | High Impact factors:
| Terrain (CAISO per unit costs) |  |  |  | 1.0X to 1.25X |  |  | 1.35X to 1.50X |  |  | 2.0X to 3.0X
| Terrain (User specified) |  |  |  |  | 1.25 |  |  | 1.5 |  |  | 2
| Population density (CAISO per unit costs) |  |  |  |  | 1.00X to 1.10X |  |  | 1.33X |  |  | 1.67X
| Population density(User specified) |  |  |  |  | 1.1 |  |  | 1.33 |  |  | 1.67
| Weather study (CAISO per unit costs) |  |  |  |  | 1.35X |  |  | 1.45X |  |  | 1.60X
| Weather study(User specified) |  |  |  |  | 1.35 |  |  | 1.45 |  |  | 1.6
| Factor Type |  |  | Explanation of Factor issues and Factor multipliers
| Terrain |  |  | Going from flat to mountainous terrain increases the cost of a transmission line. Terrain influences where structures are located, how many structures will be required and which type (strength) of structures will be required. As terrain becomes more rugged, access to the site and construction also gets more complex.
| Population density |  |  | Population and land use effect the cost of a transmission line. Structure quantities may be increased and/or made taller in more populated areas for aesthetic purposes, EMF mitigation efforts or due to crossings. Construction activities may also be impacted by physical constraints and work hour restrictions.
| Weather study |  |  | Transmission line costs increase as weather loading conditions increase. Wind and ice increase the loading on transmission structures which may require stronger structure types or an increased number of structures to reduce the span lengths.
[5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2030 and beyond
|  |  |  | Escalation Rate | 2.696% | 2.138% | 2.556% | 2.352% | 2.287% | 2.333% | 2.249% | 2.332% | 2.295% | 2.01% | 2.212% | 0.023
|  |  |  | Escalation Factors | 1 | 1.0214 | 1.0475 | 1.0721 | 1.0966 | 1.1222 | 1.1475 | 1.1742 | 1.2012 | 1.2253 | 1.2524 | 1.2812
| Contingency Factor |  | #REF!
| Contingency Factor for battery | Power | #REF!
|  | Energy | #REF!
Notes
| Contingency Factor included to account for the following considerations |  |  |  | 2018: The SDGE project has been ranked as high impact due to terrain and population, primarily driven by the complications associated with traversing the Pechanga Reservation
o Review of customer/developer existing and proposed plans (i.e. surveyed base map, street/land
improvements, profiles, grading, overhead & underground utilities, temp construction roads &
laydown/staging yards, etc.)
o Property rights study
o Right-of-way improvements/acquisitions (i.e. easements, access/maintenance roads, grading, etc.)
o GO 131-D engineering/permitting per CEQA requirements
o Non-GO 131-D Permitting (i.e. Railroad, City, County, State, Federal Agency, etc.)
o Governing regulation impacts (i.e. CPUC, FERC, OSHA, etc.)
o Environmental study and mitigations
o EMF study and potential reduction mitigations as required by the CPUC
o Geotechnical investigation and mitigations
o Surveys
o Potholing
o Traffic plans/control
o Concrete and/or asphalt repairs
o Associated SCE Substation work (i.e. breaker replacements, switch-rack position relocations, etc.)
o Associated SCE Distribution voltage under-build work (i.e. 16 kV, 12 kV, 4 kV, and secondary
conductors)
o Associated SCE Telecommunication under-build work
o Associated 3rd Party Joint Owners and renters/tenants under-build work (i.e. cable TV,
communication cable, fiber optic, etc.)
o Conflicts associated with other projects in the same geographical area or electrical system
o Availability of line outages required for construction
Unit costs exclude Licensing.
| ESS O&M | #REF! | $/kWh
| + | 1% | of EPC Cost |  | 2020: Add contingency for battery value
| Price Escalation | 2.5% |  |  | 2020: Battery cost reduction = 0%, global factor, and what it changes
| T&D Annual OPEX | #REF! |  |  | 2020: Include 2% into battery price escalation
| Inverter Replacement Cost | #REF! | $/kWh |  | 2020: Make the significant digits, 1000$ of dollars
| Battery Replacement Cost | #REF! | % Capex |  | 2020: shift it to 99 instead of 90, not take actual MW
| Annual Battery Cost Change | #REF!
| Price Stabizes in | #REF!
| Calendar Time (Year) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| O&M T&D | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Initial CapEx costs | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Incremental costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0
| Total Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| MW | 561.8036 | 6.3057 | 6.3833 | 6.4619 | 6.5415 | 6.6222 | 6.704 | 6.7869 | 6.8709 | 6.9559 | 7.0422 | 7.1296 | 7.2181 | 7.3079 | 7.3988 | 7.491 | 7.5844 | 7.679 | 7.775 | 7.8722 | 7.9708 | 8.0706 | 8.1719 | 8.2745 | 8.3784 | 8.4838 | 8.5907
| MWh | 2247.2144 | 25.223 | 25.5332 | 25.8476 | 26.1662 | 26.489 | 26.8161 | 27.1475 | 27.4834 | 27.8238 | 28.1687 | 28.5182 | 28.8725 | 29.2314 | 29.5952 | 29.9639 | 30.3375 | 30.7162 | 31.0999 | 31.4889 | 31.8831 | 32.2826 | 32.6875 | 33.0978 | 33.5138 | 33.9354 | 34.3627
| MWh uprate | 2292.1587 | 70.6717 | 71.4926 | 72.324 | 73.1658 | 74.0184 | 74.8818 | 75.7563 | 76.6418 | 77.5387 | 78.447 | 79.3669 | 80.2985 | 81.2421 | 82.1978 | 83.1658 | 84.1462 | 85.1391 | 86.1449 | 87.1636 | 88.1955 | 89.2406 | 90.2993 | 91.3716 | 92.4578 | 93.5581 | 94.6726
| Battery price | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902 | 142.6902
| Energy price | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804 | 285.3804
| Inverter replacement MW | [10 empty] | 561.8036 | 6.3057 | 6.3833 | 6.4619 | 6.5415 | 6.6222 | 6.704 | 6.7869 | 6.8709 | 6.9559 | 7.0422 | 7.1296 | 7.2181 | 7.3079 | 7.3988 | 7.491 | 7.5844
| Battery costs | 900571.1681 | 25838.6001 | 26139.4969 | 26444.2174 | 26752.8139 | 27065.3395 | 27381.848 | 27702.3942 | 22852.4778 | 23120.563 | 23392.0779 | 23667.0699 | 23945.5868 | 24227.6772 | 24513.3906 | 24802.7769 | 25095.887 | 25392.7725 | 25693.4855 | 25998.0794 | 26306.6078 | 26619.1255 | 26935.688 | 27256.3515 | 27581.1733 | 27910.2112 | 28243.5242
| Inverter replacement costs | [10 empty] | 80163.8802 | 899.7673 | 910.835 | 922.0497 | 933.4136 | 944.9288 | 956.5973 | 968.4214 | 980.4034 | 992.5454 | 1004.8497 | 1017.3187 | 1029.9547 | 1042.7601 | 1055.7374 | 1068.889 | 1082.2173
| Initial CapEx costs | #REF! 2022: #REF!
| Battery replacement costs | #REF! 2042: 450285.5841; #REF! 2043: 12919.3; #REF! 2044: 13069.7484; #REF! 2045: 13222.1087; #REF! 2046: 13376.4069; #REF! 2047: 13532.6697; #REF! 2048: 13690.924
| O&M ESS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| O&M ESS Augment |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total O&M Costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total costs | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| NPV | #REF! 2022: #REF!
| Aggregate | #REF! 2022: #REF!

## 17 - Cost Benefit (hidden)
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 50888.05 | 51484.5538 | 52081.0577 | 52677.5615 | 53274.0654 | 53870.5692 | 54467.0731 | 55063.5769 | 55660.0808 | 56256.5846 | 56853.0885 | 57449.5923 | 58046.0962 | 58642.6 | 59239.1038 | 59835.6077 | 60432.1115 | 61028.6154 | 61625.1192 | 62221.6231 | 62818.1269 | 63414.6308 | 64011.1346 | 64607.6385 | 65204.1423 | 65800.6462 | 66397.15
N-1 |  | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 |  | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 |  | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 |  | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 |  | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-1 |  | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 |  | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 |  | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 |  | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 |  | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 |  | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 |  | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 30% Distributed Energy Storage | Losses (MWh) | 38659.7 | 39104.55 | 39252.8333 | 39104.55 | 39703.4761 | 40302.4022 | 40901.3283 | 41500.2543 | 42099.1804 | 42698.1065 | 43297.0326 | 43895.9587 | 44494.8848 | 45093.8109 | 45692.737 | 46291.663 | 46890.5891 | 47489.5152 | 48088.4413 | 48687.3674 | 49286.2935 | 49885.2196 | 50484.1457 | 51083.0717 | 51681.9978 | 52280.9239 | 52879.85
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | Available Flex-1 | 8.07 | 484.212 | 960.354 | 1436.496 | 1912.638 | 2388.7801 | 2864.9221 | 3341.0641 | 3817.2061 | 4293.3481 | 4769.4901 | 5245.6321 | 5721.7741 | 6197.9162 | 6674.0582 | 7150.2002 | 7626.3422 | 8102.4842 | 8578.6262 | 9054.7682 | 9530.9102 | 10007.0522 | 10483.1943 | 10959.3363 | 11435.4783 | 11911.6203 | 12387.7623
N-1 |  | Available Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component |  |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 122489.8233 | Losses (MWh) | 12228.35 | 12380.0038 | 12828.2244 | 13573.0115 | 13570.5893 | 13568.1671 | 13565.7448 | 13563.3226 | 13560.9003 | 13558.4781 | 13556.0559 | 13553.6336 | 13551.2114 | 13548.7891 | 13546.3669 | 13543.9446 | 13541.5224 | 13539.1002 | 13536.6779 | 13534.2557 | 13531.8334 | 13529.4112 | 13526.989 | 13524.5667 | 13522.1445 | 13519.7222 | 13517.3
| 6043531.5976 | Losses ($) | 489134 | 507580.1577 | 539106.1287 | 584665.9552 | 599175.656 | 614045.4257 | 629284.1991 | 644901.1327 | 660905.6104 | 677307.2488 | 694115.9031 | 711341.6731 | 728994.9091 | 747086.2184 | 765626.4714 | 784626.8081 | 804098.6451 | 824053.6822 | 844503.9095 | 865461.6146 | 886939.39 | 908950.1407 | 931507.0918 | 954623.7966 | 978314.1447 | 1002592.3704 | 1027473.061
N-1 | 10600.9528 | EENS | 40 | 71.8333 | 103.6667 | 135.5 | 167.3333 | 199.1667 | 231 | 348.1 | 465.2 | 582.3 | 699.4 | 988.65 | 1277.9 | 1567.15 | 1856.4 | 2145.65 | 2434.9 | 3114.97 | 3795.04 | 4475.11 | 5155.18 | 5262.7 | 6057.28 | 6851.86 | 7646.44 | 8441.02 | 9235.6
N-1 | 289.0343 | IP | 6 | 8.8833 | 11.7667 | 14.65 | 17.5333 | 20.4167 | 23.3 | 26.25 | 29.2 | 32.15 | 35.1 | 39.5 | 43.9 | 48.3 | 52.7 | 57.1 | 61.5 | 63.48 | 65.46 | 67.44 | 69.42 | 71.4 | 82.8 | 94.2 | 105.6 | 117 | 128.4
N-1 | 1251.2075 | SAIDI | 0.45604 | 1.1324 | 1.8087 | 2.4851 | 3.1615 | 3.8378 | 4.5142 | 9.7534 | 14.9927 | 20.232 | 25.4713 | 54.1368 | 82.8022 | 111.4677 | 140.1331 | 168.7986 | 197.464 | 305.5991 | 413.7342 | 521.8693 | 630.0044 | 738.1395 | 977.3569 | 1216.5742 | 1455.7915 | 1695.0088 | 1934.2261
N-1 | 9.345 | SAIFI | 0.030923 | 0.057591 | 0.084259 | 0.11093 | 0.13759 | 0.16426 | 0.19093 | 0.29587 | 0.40082 | 0.50576 | 0.61071 | 0.8724 | 1.1341 | 1.3958 | 1.6575 | 1.9191 | 2.1808 | 2.7007 | 3.2205 | 3.7403 | 4.2602 | 4.78 | 5.5136 | 6.2472 | 6.9808 | 7.7144 | 8.448
N-1 | 756.0078 | PFD | 28 | 33.3333 | 38.6667 | 44 | 49.3333 | 54.6667 | 60 | 67 | 74 | 81 | 88 | 97.8333 | 107.6667 | 117.5 | 127.3333 | 137.1667 | 147 | 158.4 | 169.8 | 181.2 | 192.6 | 204 | 215.4 | 226.8 | 238.2 | 249.6 | 261
N-1 | #REF! | Available Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-1 | #REF! | Available Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
N-0 | 23252.3884 | EENS | 129 | 258.75 | 388.5 | 518.25 | 648 | 777.75 | 907.5 | 1246.7 | 1585.9 | 1925.1 | 2264.3 | 2843.6833 | 3423.0667 | 4002.45 | 4581.8333 | 5161.2167 | 5740.6 | 6570 | 7399.4 | 8228.8 | 9058.2 | 9887.6 | 10814.56 | 11741.52 | 12668.48 | 13595.44 | 14522.4
N-0 | 1446.8726 | IP | 42.2 | 57.0667 | 71.9333 | 86.8 | 101.6667 | 116.5333 | 131.4 | 146.05 | 160.7 | 175.35 | 190 | 205 | 220 | 235 | 250 | 265 | 280 | 293.68 | 307.36 | 321.04 | 334.72 | 348.4 | 360.84 | 373.28 | 385.72 | 398.16 | 410.6
N-0 | 1932.2817 | SAIDI | 0.68645 | 3.6305 | 6.5745 | 9.5186 | 12.4626 | 15.4066 | 18.3507 | 36.0539 | 53.7571 | 71.4603 | 89.1635 | 144.5626 | 199.9618 | 255.3609 | 310.76 | 366.1592 | 421.5583 | 551.9171 | 682.276 | 812.6348 | 942.9936 | 1073.3524 | 1297.6248 | 1521.8972 | 1746.1697 | 1970.4421 | 2194.7145
N-0 | 24.7468 | SAIFI | 0.13729 | 0.27538 | 0.41347 | 0.55156 | 0.68965 | 0.82773 | 0.96582 | 1.3268 | 1.6878 | 2.0488 | 2.4098 | 3.0264 | 3.6431 | 4.2597 | 4.8763 | 5.4929 | 6.1095 | 6.9922 | 7.8749 | 8.7577 | 9.6404 | 10.5231 | 11.5096 | 12.4961 | 13.4827 | 14.4692 | 15.4557
N-0 | 308.8106 | PFD | 5 | 7.3333 | 9.6667 | 12 | 14.3333 | 16.6667 | 19 | 23.5 | 28 | 32.5 | 37 | 42.3333 | 47.6667 | 53 | 58.3333 | 63.6667 | 69 | 75.6 | 82.2 | 88.8 | 95.4 | 102 | 110 | 118 | 126 | 134 | 142
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-0) | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | EENS | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical(N-1) | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate | Value for Flex-2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Aggregate |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Project Cost |  | #REF!
Benefit-Cost Ratio |  | #REF!