## Summary
Summary of Cost-Benefit analysis
($ millions)
# | Project | Total Nominal Capital Cost | Present Value of Revenue Requirement | Benefit($M) | Benefit-Cost Ratio | # | Project | Cost-Benefit Ratio
1 | Alberhill System Project | 545 | 545 | 4444.4903 | 8.155 | 8 | Mira Loma | 0.10849
2 | SDG&E | 540 | 469 | 2208.9614 | 4.7099 | 1 | Alberhill System Project | 0.12262
3 | Valley South to Valley North to Vista | 285 | 270 | 1356.2233 | 5.023 | 6 | Valley South to Valley North and Distributed BESS in Valley South | 0.13749
4 | Centralized BESS in Valley South | 1004 | 417 | 2356.3326 | 5.6507 | 13 | Valley South to Valley North | 0.13749
5 | Mira Loma and Centralized BESS in Valley South | 881 | 429 | 2765.5471 | 6.4465 | 5 | Mira Loma and Centralized BESS in Valley South | 0.15512
6 | Valley South to Valley North and Distributed BESS in Valley South | 190 | 185 | 1345.5677 | 7.2733 | 10 | Valley South to Valley North and Centralized BESS in Valley South and Valley North | 0.17613
7 | Menifee | 358 | 315 | 1619.2608 | 5.1405 | 7 | Menifee | 0.19453
8 | Mira Loma | 328 | 290 | 2673.0526 | 9.2174 | 12 | SDG&E and Centralized BESS in Valley South | 0.19628
9 | SCE Orange County | 951 | 806 | 3720.4071 | 4.6159 | 4 | Centralized BESS in Valley South | 0.17697
10 | Valley South to Valley North and Centralized BESS in Valley South and Valley North | 538 | 239 | 1356.9691 | 5.6777 | 11 | Valley South to Valley North to Vista and Centralized BESS in Valley South | 0.19908
11 | Valley South to Valley North to Vista and Centralized BESS in Valley South | 285 | 270 | 1356.2233 | 5.023 | 3 | Valley South to Valley North to Vista | 0.19908
12 | SDG&E and Centralized BESS in Valley South | 685 | 504 | 2567.8099 | 5.0949 | 2 | SDG&E | 0.21232
13 | Valley South to Valley North | 190 | 185 | 1345.5677 | 7.2733 | 9 | SCE Orange County | 0.21664
Note on A3: In this spreadsheet all relevant benefits associated with project savings have been monetized and alternatives are ranked using their Cost-to-Benefit ratio performance.

## Incr. C-B Reliability Indices
Incremental Cost-Benefit analysis taking into consideration Non-Monetized Benefits of reliability indices.
# | Project | Present Value | Aggregate | [25 empty] | For Calculations only
0 | Baseline | 0 | 0 | [25 empty] | Category |  |  |  | NPV of benefits between Project and Baseline | NPV of Project Performance
6 | Valley South to Valley North and Distributed BESS in Valley South | 185 | 328 | [25 empty] | N-1 | EENS | 1 | N-1 EENS 1 | 1000.4962 | 8.4335
13 | Valley South to Valley North | 185.2 | 951 | [25 empty] | N-1 | IP | 1 | N-1 IP 1 | 96.6191 | 3.5515
10 | Valley South to Valley North and Centralized BESS in Valley South and Valley North | 239 | 540 | [25 empty] | N-1 | SAIDI | 1 | N-1 SAIDI 1 | 73.2552 | 0.081394
3 | Valley South to Valley North to Vista | 270 | 538 | [25 empty] | N-1 | SAIFI | 1 | N-1 SAIFI 1 | 1.4508 | 0.021332
11 | Valley South to Valley North to Vista and Centralized BESS in Valley South | 270 | 685 | [25 empty] | N-1 | PFD | 1 | N-1 PFD 1 | 314.0886 | 1.8695
8 | Mira Loma | 290 | 881 | [25 empty] | N-1 | Available Flex-1 | 1 | N-1 Available Flex-1 1 | 133706.0462 | 0
7 | Menifee | 315 | 358 | [25 empty] | N-1 | Available Flex-2-1 | 1 | N-1 Available Flex-2-1 1 | 1769189.9238 | 90917.1207
4 | Centralized BESS in Valley South | 417 | 273 | [25 empty] | N-1 | Available Flex-2-2 | 1 | N-1 Available Flex-2-2 1 | 694321.8706 | 0
5 | Mira Loma and Centralized BESS in Valley South | 429 | 285 | [25 empty] | N-0 | EENS | 1 | N-0 EENS 1 | 3662.4319 | 0
2 | SDG&E | 469 | 190 | [25 empty] | N-0 | IP | 1 | N-0 IP 1 | 603.3371 | 0
12 | SDG&E and Centralized BESS in Valley South | 504 | 545 | [25 empty] | N-0 | SAIDI | 1 | N-0 SAIDI 1 | 54.0898 | 0
1 | Alberhill System Project | 545 | 187 | [25 empty] | N-0 | SAIFI | 1 | N-0 SAIFI 1 | 2.9079 | 0
9 | SCE Orange County | 806 | 1004 | [25 empty] | N-0 | PFD | 1 | N-0 PFD 1 | 81.9765 | 0
[29 empty] | N-1 | EENS | 2 | N-1 EENS 2 | 1008.9296 | 0
[29 empty] | N-1 | IP | 2 | N-1 IP 2 | 100.1707 | 0
Present Value of Benefits by Project | [28 empty] | N-1 | SAIDI | 2 | N-1 SAIDI 2 | 73.3366 | 0
|  | Alberhill System Project | SDG&E | Valley South to Valley North to Vista | Centralized BESS in Valley South | Mira Loma and Centralized BESS in Valley South | Valley South to Valley North and Distributed BESS in Valley South | Menifee | Mira Loma | SCE Orange County | Valley South to Valley North and Centralized BESS in Valley South and Valley North | Valley South to Valley North to Vista and Centralized BESS in Valley South | SDG&E and Centralized BESS in Valley South | Valley South to Valley North | [14 empty] | N-1 | SAIFI | 2 | N-1 SAIFI 2 | 1.4722 | 0
Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | [14 empty] | N-1 | PFD | 2 | N-1 PFD 2 | 315.9581 | 0
N-1 | EENS | 1000.4962 | 1008.9296 | 114.4291 | 1008.9296 | 753.6406 | 114.4291 | 114.4291 | 503.7157 | 838.7877 | 114.4291 | 114.4291 | 1008.9296 | 114.4291 | [14 empty] | N-1 | Available Flex-1 | 2 | N-1 Available Flex-1 2 | 60203.8892 | 73502.1569
N-1 | IP | 96.6191 | 100.1707 | -30.4126 | 100.1707 | 43.6672 | -30.4126 | -30.4126 | 24.5703 | 79.804 | -30.4126 | -30.4126 | 100.1707 | -30.4126 | [14 empty] | N-1 | Available Flex-2-1 | 2 | N-1 Available Flex-2-1 2 | 1272587.0328 | 587520.0117
N-1 | SAIDI | 73.2552 | 73.3366 | 54.4087 | 73.3366 | 69.1726 | 54.4087 | 54.4087 | 64.2375 | 71.5256 | 54.4087 | 54.4087 | 73.3366 | 54.4087 | [14 empty] | N-1 | Available Flex-2-2 | 2 | N-1 Available Flex-2-2 2 | 526663.8571 | 167658.0135
N-1 | SAIFI | 1.4508 | 1.4722 | 0.65104 | 1.4722 | 1.2092 | 0.65104 | 0.65104 | 0.95698 | 1.2897 | 0.65104 | 0.65104 | 1.4722 | 0.65104 | [14 empty] | N-0 | EENS | 2 | N-0 EENS 2 | 3662.2031 | 0.22883
N-1 | PFD | 314.0886 | 315.9581 | 225.5303 | 315.9581 | 269.1878 | 225.5303 | 225.5303 | 268.006 | 271.7551 | 225.5303 | 225.5303 | 315.9581 | 225.5303 | [14 empty] | N-0 | IP | 2 | N-0 IP 2 | 603.1082 | 0.22883
N-1 | Available Flex-1 | 133706.0462 | 60203.8892 | 39141.4455 | 82124.1153 | 85504.239 | 39141.4455 | 39141.4455 | 83412.309 | 113296.0689 | 39141.4455 | 39141.4455 | 75415.3058 | 39141.4455 | [14 empty] | N-0 | SAIDI | 2 | N-0 SAIDI 2 | 54.0896 | 0.0001989
N-1 | Available Flex-2-1 | 1769189.9238 | 1272587.0328 | 0 | 0.029234 | 499595.179 | 0 | 1132819.4222 | 499595.179 | 1296335.2715 | 0 | 0 | 1272587.0328 | 0 | [14 empty] | N-0 | SAIFI | 2 | N-0 SAIFI 2 | 2.9077 | 0.0001989
N-1 | Available Flex-2-2 | 694321.8706 | 526663.8571 | 479183.4057 | 3460.9343 | 451168.6674 | 479183.4057 | 479183.4057 | 451168.6674 | 557015.6362 | 479183.4057 | 479183.4057 | 526663.8571 | 479183.4057 | [14 empty] | N-0 | PFD | 2 | N-0 PFD 2 | 81.9002 | 0.076278
N-0 | EENS | 3662.4319 | 3662.2031 | 3651.1526 | 3662.4319 | 3662.4319 | 3422.1306 | 3662.4319 | 3157.218 | 3662.4319 | 3662.4319 | 3651.1526 | 3662.4319 | 3422.1306 | [14 empty] | N-1 | EENS | 3 | N-1 EENS 3 | 114.4291 | 894.5005
N-0 | IP | 603.3371 | 603.1082 | 597.1428 | 603.3371 | 603.3371 | 527.3168 | 603.3371 | 493.8907 | 603.3371 | 603.3371 | 597.1428 | 603.3371 | 527.3168 | [14 empty] | N-1 | IP | 3 | N-1 IP 3 | -30.4126 | 130.5833
N-0 | SAIDI | 54.0898 | 54.0896 | 54.0416 | 54.0898 | 54.0898 | 49.0833 | 54.0898 | 37.8706 | 54.0898 | 54.0898 | 54.0416 | 54.0898 | 49.0833 | [14 empty] | N-1 | SAIDI | 3 | N-1 SAIDI 3 | 54.4087 | 18.928
N-0 | SAIFI | 2.9079 | 2.9077 | 2.8981 | 2.9079 | 2.9079 | 2.6068 | 2.9079 | 2.1996 | 2.9079 | 2.9079 | 2.8981 | 2.9079 | 2.6068 | [14 empty] | N-1 | SAIFI | 3 | N-1 SAIFI 3 | 0.65104 | 0.82113
N-0 | PFD | 81.9765 | 81.9002 | 80.9706 | 81.9765 | 81.9765 | 73.8974 | 81.9765 | 74.7266 | 81.9765 | 81.9765 | 80.9706 | 81.9765 | 73.8974 | [14 empty] | N-1 | PFD | 3 | N-1 PFD 3 | 225.5303 | 90.4278
[29 empty] | N-1 | Available Flex-1 | 3 | N-1 Available Flex-1 3 | 39141.4455 | 94564.6006
Ranking of Projects by Cost | [28 empty] | N-1 | Available Flex-2-1 | 3 | N-1 Available Flex-2-1 3 | 0 | 1860107.0445
[29 empty] | N-1 | Available Flex-2-2 | 3 | N-1 Available Flex-2-2 3 | 479183.4057 | 215138.4648
Category |  | 0 | 6 | 13 | 10 | 3 | 11 | 8 | 7 | 4 | 5 | 2 | 12 | 1 | 9 | [13 empty] | N-0 | EENS | 3 | N-0 EENS 3 | 3651.1526 | 11.2793
[29 empty] | N-0 | IP | 3 | N-0 IP 3 | 597.1428 | 6.1943
[29 empty] | N-0 | SAIDI | 3 | N-0 SAIDI 3 | 54.0416 | 0.048256
Category |  | 1: Alternative selection | [13 empty] | Preferred Trend | N-0 | SAIFI | 3 | N-0 SAIFI 3 | 2.8981 | 0.0098107
|  | 1: 0 --> 6; 3: 6 --> 13; 5: 6 --> 10; 7: 10 --> 3; 9: 10 --> 11; 11: 10 --> 8; 13: 8 --> 7 |  | 8 --> 4 |  | 8 --> 5 |  | 8 --> 2 |  | 8 --> 12 |  | 8 --> 1 |  | 1 --> 9 |  |  | N-0 | PFD | 3 | N-0 PFD 3 | 80.9706 | 1.0059
|  | 0 | 6 | 6 | 13 | 6 | 10 | 10 | 3 | 10 | 11 | 10 | 8 | 8 | 7 | 8 | 4 | 8 | 5 | 8 | 2 | 8 | 12 | 8 | 1 | 1 | 9 |  | N-1 | EENS | 4 | N-1 EENS 4 | 1008.9296 | 0
N-1 | EENS | 1: -0.61854; 3: 0; 5: 0; 7: 0; 9: 0; 11: -7.8328; 13: 15.9789 |  | -3.8979 |  | -1.7247 |  | -2.7655 |  | -2.3132 |  | -1.9082 |  | 0.61957 |  | ↓ | N-1 | IP | 4 | N-1 IP 4 | 100.1707 | 0
N-1 | IP | 1: 0.16439; 3: 0; 5: 0; 7: 0; 9: 0; 11: -0.70662; 13: 1.4415 |  | -0.74446 |  | -0.27369 |  | -0.52819 |  | -0.4418 |  | -0.35684 |  | 0.064426 |  | ↓ | N-1 | SAIDI | 4 | N-1 SAIDI 4 | 73.3366 | 0
N-1 | SAIDI | 1: -0.2941; 3: 0; 5: 0; 7: 0; 9: 0; 11: -0.24403; 13: 0.49782 |  | -0.051043 |  | -0.016679 |  | -0.036215 |  | -0.030292 |  | -0.025102 |  | 0.006627 |  | ↓ | N-1 | SAIFI | 4 | N-1 SAIFI 4 | 1.4722 | 0
N-1 | SAIFI | 1: -0.0035192; 3: 0; 5: 0; 7: 0; 9: 0; 11: -0.006383; 13: 0.013021 |  | -0.0039023 |  | -0.0016732 |  | -0.0027687 |  | -0.0023159 |  | -0.0018599 |  | 0.00061743 |  | ↓ | N-1 | PFD | 4 | N-1 PFD 4 | 315.9581 | 0
N-1 | PFD | 1: -1.2191; 3: 0; 5: 0; 7: 0; 9: 0; 11: -0.96893; 13: 1.9766 |  | -0.32293 |  | 0.041424 |  | -0.22912 |  | -0.19165 |  | -0.1535 |  | 0.1622 |  | ↓ | N-1 | Available Flex-1 | 4 | N-1 Available Flex-1 4 | 82124.1153 | 51581.9308
N-1 | Available Flex-1 | 1: -211.5754; 3: 0; 5: 0; 7: 0; 9: 0; 11: -868.0561; 13: 1770.8345 |  | 10.1433 |  | -15.0499 |  | 129.656 |  | 37.3692 |  | -197.2303 |  | 78.1991 |  | ↓ | N-1 | Available Flex-2-1 | 4 | N-1 Available Flex-2-1 4 | 0.029234 | 1860107.0153
N-1 | Available Flex-2-1 | 1: 0; 3: 0; 5: 0; 7: 0; 9: 0; 11: -9795.9839; 13: -25328.9697 |  | 3933.8201 |  | 0 |  | -4318.3902 |  | -3612.1115 |  | -4978.8029 |  | 1811.7036 |  | ↓ | N-1 | Available Flex-2-2 | 4 | N-1 Available Flex-2-2 4 | 3460.9343 | 690860.9363
N-1 | Available Flex-2-2 | 1: -2590.1806; 3: 0; 5: 0; 7: 0; 9: 0; 11: 549.3086; 13: -1120.5895 |  | 3525.2577 |  | 0 |  | -421.7608 |  | -352.7813 |  | -953.542 |  | 526.0775 |  | ↓ | N-0 | EENS | 4 | N-0 EENS 4 | 3662.4319 | 0
N-0 | EENS | 1: -18.498; 3: 0; 5: -4.45; 7: 0.36385; 9: 0.44026; 11: 6.9017; 13: -14.0795 |  | -2.7716 |  | -2.5323 |  | -1.9651 |  | -1.6448 |  | -1.3803 |  | 0 |  | ↓ | N-0 | IP | 4 | N-0 IP 4 | 603.3371 | 0
N-0 | IP | 1: -2.8504; 3: 0; 5: -1.4078; 7: 0.19982; 9: 0.19982; 11: 2.146; 13: -4.3779 |  | -0.86178 |  | -0.78738 |  | -0.61015 |  | -0.51143 |  | -0.4292 |  | 0 |  | ↓ | N-0 | SAIDI | 4 | N-0 SAIDI 4 | 54.0898 | 0
N-0 | SAIDI | 1: -0.26532; 3: 0; 5: -0.092713; 7: 0.0015566; 9: 0.0015566; 11: 0.31802; 13: -0.64877 |  | -0.12771 |  | -0.11668 |  | -0.090609 |  | -0.075791 |  | -0.063605 |  | 0 |  | ↓ | N-0 | SAIFI | 4 | N-0 SAIFI 4 | 2.9079 | 0
N-0 | SAIFI | 1: -0.014091; 3: 0; 5: -0.0055756; 7: 0.00031647; 9: 0.00031647; 11: 0.013888; 13: -0.028331 |  | -0.0055771 |  | -0.0050956 |  | -0.0039558 |  | -0.0033097 |  | -0.0027776 |  | 0 |  | ↓ | N-0 | PFD | 4 | N-0 PFD 4 | 81.9765 | 0
N-0 | PFD | 1: -0.39945; 3: 0; 5: -0.14961; 7: 0.032449; 9: 0.032449; 11: 0.29872; 13: -0.60939 |  | -0.11996 |  | -0.1096 |  | -0.084685 |  | -0.071191 |  | -0.059745 |  | 0 |  | ↓ | N-1 | EENS | 5 | N-1 EENS 5 | 753.6406 | 255.2891
Decision to move forward (Y/N) | [15 empty] | N |  | N |  | N |  | N |  | Y |  | N |  |  | N-1 | IP | 5 | N-1 IP 5 | 43.6672 | 56.5035 | bar: 1; 3; 5; 7; 9; 11; 13
[29 empty] | N-1 | SAIDI | 5 | N-1 SAIDI 5 | 69.1726 | 4.164
[29 empty] | N-1 | SAIFI | 5 | N-1 SAIFI 5 | 1.2092 | 0.26301
Category |  | 1: Baseline - Alberhill | [14 empty] | N-1 | PFD | 5 | N-1 PFD 5 | 269.1878 | 46.7703
|  | 1: 0 --> 1 | [14 empty] | N-1 | Available Flex-1 | 5 | N-1 Available Flex-1 5 | 85504.239 | 48201.8072
|  | 1: 0; 2: 1 | [14 empty] | N-1 | Available Flex-2-1 | 5 | N-1 Available Flex-2-1 5 | 499595.179 | 1360511.8655
N-1 | EENS | 1: -1.8358 | [14 empty] | N-1 | Available Flex-2-2 | 5 | N-1 Available Flex-2-2 5 | 451168.6674 | 243153.2031
N-1 | IP | 1: -0.17728 | [14 empty] | N-0 | EENS | 5 | N-0 EENS 5 | 3662.4319 | 0
N-1 | SAIDI | 1: -0.13441 | [14 empty] | N-0 | IP | 5 | N-0 IP 5 | 603.3371 | 0
N-1 | SAIFI | 1: -0.0026621 | [14 empty] | N-0 | SAIDI | 5 | N-0 SAIDI 5 | 54.0898 | 0
N-1 | PFD | 1: -0.57631 | [14 empty] | N-0 | SAIFI | 5 | N-0 SAIFI 5 | 2.9079 | 0
N-1 | Available Flex-1 | 1: -245.3322 | [14 empty] | N-0 | PFD | 5 | N-0 PFD 5 | 81.9765 | 0
N-1 | Available Flex-2-1 | 1: -3246.22 | [14 empty] | N-1 | EENS | 0 | N-1 EENS 0 | 0 | 1008.9296
N-1 | Available Flex-2-2 | 1: -1273.9851 | [14 empty] | N-1 | IP | 0 | N-1 IP 0 | 0 | 100.1707
N-0 | EENS | 1: -6.7201 | [14 empty] | N-1 | SAIDI | 0 | N-1 SAIDI 0 | 0 | 73.3366
N-0 | IP | 1: -1.107 | [14 empty] | N-1 | SAIFI | 0 | N-1 SAIFI 0 | 0 | 1.4722
N-0 | SAIDI | 1: -0.099247 | [14 empty] | N-1 | PFD | 0 | N-1 PFD 0 | 0 | 315.9581
N-0 | SAIFI | 1: -0.0053355 | [14 empty] | N-1 | Available Flex-1 | 0 | N-1 Available Flex-1 0 | 0 | 133706.0462
N-0 | PFD | 1: -0.15042 | [14 empty] | N-1 | Available Flex-2-1 | 0 | N-1 Available Flex-2-1 0 | 0 | 1860107.0445
[29 empty] | N-1 | Available Flex-2-2 | 0 | N-1 Available Flex-2-2 0 | 0 | 694321.8706
[29 empty] | N-0 | EENS | 0 | N-0 EENS 0 | 0 | 3662.4319
[29 empty] | N-0 | IP | 0 | N-0 IP 0 | 0 | 603.3371
[29 empty] | N-0 | SAIDI | 0 | N-0 SAIDI 0 | 0 | 54.0898
[29 empty] | N-0 | SAIFI | 0 | N-0 SAIFI 0 | 0 | 2.9079
[29 empty] | N-0 | PFD | 0 | N-0 PFD 0 | 0 | 81.9765
[29 empty] | N-1 | EENS | 6 | N-1 EENS 6 | 114.4291 | 894.5005
[29 empty] | N-1 | IP | 6 | N-1 IP 6 | -30.4126 | 130.5833
[29 empty] | N-1 | SAIDI | 6 | N-1 SAIDI 6 | 54.4087 | 18.928
[29 empty] | N-1 | SAIFI | 6 | N-1 SAIFI 6 | 0.65104 | 0.82113
[29 empty] | N-1 | PFD | 6 | N-1 PFD 6 | 225.5303 | 90.4278
[29 empty] | N-1 | Available Flex-1 | 6 | N-1 Available Flex-1 6 | 39141.4455 | 94564.6006
[29 empty] | N-1 | Available Flex-2-1 | 6 | N-1 Available Flex-2-1 6 | 0 | 1860107.0445
[29 empty] | N-1 | Available Flex-2-2 | 6 | N-1 Available Flex-2-2 6 | 479183.4057 | 215138.4648
[29 empty] | N-0 | EENS | 6 | N-0 EENS 6 | 3422.1306 | 240.3013
[29 empty] | N-0 | IP | 6 | N-0 IP 6 | 527.3168 | 76.0203
[29 empty] | N-0 | SAIDI | 6 | N-0 SAIDI 6 | 49.0833 | 5.0065
[29 empty] | N-0 | SAIFI | 6 | N-0 SAIFI 6 | 2.6068 | 0.30108
[29 empty] | N-0 | PFD | 6 | N-0 PFD 6 | 73.8974 | 8.0791
[29 empty] | N-1 | EENS | 7 | N-1 EENS 7 | 114.4291 | 894.5005
[29 empty] | N-1 | IP | 7 | N-1 IP 7 | -30.4126 | 130.5833
[29 empty] | N-1 | SAIDI | 7 | N-1 SAIDI 7 | 54.4087 | 18.928
[29 empty] | N-1 | SAIFI | 7 | N-1 SAIFI 7 | 0.65104 | 0.82113
[29 empty] | N-1 | PFD | 7 | N-1 PFD 7 | 225.5303 | 90.4278
[29 empty] | N-1 | Available Flex-1 | 7 | N-1 Available Flex-1 7 | 39141.4455 | 94564.6006
[29 empty] | N-1 | Available Flex-2-1 | 7 | N-1 Available Flex-2-1 7 | 1132819.4222 | 727287.6223
[29 empty] | N-1 | Available Flex-2-2 | 7 | N-1 Available Flex-2-2 7 | 479183.4057 | 215138.4648
[29 empty] | N-0 | EENS | 7 | N-0 EENS 7 | 3662.4319 | 0
[29 empty] | N-0 | IP | 7 | N-0 IP 7 | 603.3371 | 0
[29 empty] | N-0 | SAIDI | 7 | N-0 SAIDI 7 | 54.0898 | 0
[29 empty] | N-0 | SAIFI | 7 | N-0 SAIFI 7 | 2.9079 | 0
[29 empty] | N-0 | PFD | 7 | N-0 PFD 7 | 81.9765 | 0
[29 empty] | N-1 | EENS | 8 | N-1 EENS 8 | 503.7157 | 495.029
[29 empty] | N-1 | IP | 8 | N-1 IP 8 | 24.5703 | 94.5459
[29 empty] | N-1 | SAIDI | 8 | N-1 SAIDI 8 | 64.2375 | 6.4825
[29 empty] | N-1 | SAIFI | 8 | N-1 SAIFI 8 | 0.95698 | 0.4956
[29 empty] | N-1 | PFD | 8 | N-1 PFD 8 | 268.006 | 41.0123
[29 empty] | N-1 | Available Flex-1 | 8 | N-1 Available Flex-1 8 | 83412.309 | 50293.7372
[29 empty] | N-1 | Available Flex-2-1 | 8 | N-1 Available Flex-2-1 8 | 499595.179 | 1360511.8655
[29 empty] | N-1 | Available Flex-2-2 | 8 | N-1 Available Flex-2-2 8 | 451168.6674 | 243153.2031
[29 empty] | N-0 | EENS | 8 | N-0 EENS 8 | 3157.218 | 351.9884
[29 empty] | N-0 | IP | 8 | N-0 IP 8 | 493.8907 | 109.4464
[29 empty] | N-0 | SAIDI | 8 | N-0 SAIDI 8 | 37.8706 | 16.2192
[29 empty] | N-0 | SAIFI | 8 | N-0 SAIFI 8 | 2.1996 | 0.70829
[29 empty] | N-0 | PFD | 8 | N-0 PFD 8 | 74.7266 | 15.2349
[29 empty] | N-1 | EENS | 9 | N-1 EENS 9 | 838.7877 | 170.1419
[29 empty] | N-1 | IP | 9 | N-1 IP 9 | 79.804 | 20.3667
[29 empty] | N-1 | SAIDI | 9 | N-1 SAIDI 9 | 71.5256 | 1.811
[29 empty] | N-1 | SAIFI | 9 | N-1 SAIFI 9 | 1.2897 | 0.18248
[29 empty] | N-1 | PFD | 9 | N-1 PFD 9 | 271.7551 | 44.203
[29 empty] | N-1 | Available Flex-1 | 9 | N-1 Available Flex-1 9 | 113296.0689 | 20409.9772
[29 empty] | N-1 | Available Flex-2-1 | 9 | N-1 Available Flex-2-1 9 | 1296335.2715 | 563771.7729
[29 empty] | N-1 | Available Flex-2-2 | 9 | N-1 Available Flex-2-2 9 | 557015.6362 | 137306.2343
[29 empty] | N-0 | EENS | 9 | N-0 EENS 9 | 3662.4319 | 0
[29 empty] | N-0 | IP | 9 | N-0 IP 9 | 603.3371 | 0
[29 empty] | N-0 | SAIDI | 9 | N-0 SAIDI 9 | 54.0898 | 0
[29 empty] | N-0 | SAIFI | 9 | N-0 SAIFI 9 | 2.9079 | 0
[29 empty] | N-0 | PFD | 9 | N-0 PFD 9 | 81.9765 | 0
[29 empty] | N-1 | EENS | 10 | N-1 EENS 10 | 114.4291 | 894.5005
[29 empty] | N-1 | IP | 10 | N-1 IP 10 | -30.4126 | 130.5833
[29 empty] | N-1 | SAIDI | 10 | N-1 SAIDI 10 | 54.4087 | 18.928
[29 empty] | N-1 | SAIFI | 10 | N-1 SAIFI 10 | 0.65104 | 0.82113
[29 empty] | N-1 | PFD | 10 | N-1 PFD 10 | 225.5303 | 90.4278
[29 empty] | N-1 | Available Flex-1 | 10 | N-1 Available Flex-1 10 | 39141.4455 | 94564.6006
[29 empty] | N-1 | Available Flex-2-1 | 10 | N-1 Available Flex-2-1 10 | 0 | 1860107.0445
[29 empty] | N-1 | Available Flex-2-2 | 10 | N-1 Available Flex-2-2 10 | 479183.4057 | 215138.4648
[29 empty] | N-0 | EENS | 10 | N-0 EENS 10 | 3662.4319 | 0
[29 empty] | N-0 | IP | 10 | N-0 IP 10 | 603.3371 | 0
[29 empty] | N-0 | SAIDI | 10 | N-0 SAIDI 10 | 54.0898 | 0
[29 empty] | N-0 | SAIFI | 10 | N-0 SAIFI 10 | 2.9079 | 0
[29 empty] | N-0 | PFD | 10 | N-0 PFD 10 | 81.9765 | 0
[29 empty] | N-1 | EENS | 11 | N-1 EENS 11 | 114.4291 | 894.5005
[29 empty] | N-1 | IP | 11 | N-1 IP 11 | -30.4126 | 130.5833
[29 empty] | N-1 | SAIDI | 11 | N-1 SAIDI 11 | 54.4087 | 18.928
[29 empty] | N-1 | SAIFI | 11 | N-1 SAIFI 11 | 0.65104 | 0.82113
[29 empty] | N-1 | PFD | 11 | N-1 PFD 11 | 225.5303 | 90.4278
[29 empty] | N-1 | Available Flex-1 | 11 | N-1 Available Flex-1 11 | 39141.4455 | 94564.6006
[29 empty] | N-1 | Available Flex-2-1 | 11 | N-1 Available Flex-2-1 11 | 0 | 1860107.0445
[29 empty] | N-1 | Available Flex-2-2 | 11 | N-1 Available Flex-2-2 11 | 479183.4057 | 215138.4648
[29 empty] | N-0 | EENS | 11 | N-0 EENS 11 | 3651.1526 | 13.6479
[29 empty] | N-0 | IP | 11 | N-0 IP 11 | 597.1428 | 6.1943
[29 empty] | N-0 | SAIDI | 11 | N-0 SAIDI 11 | 54.0416 | 0.048256
[29 empty] | N-0 | SAIFI | 11 | N-0 SAIFI 11 | 2.8981 | 0.0098107
[29 empty] | N-0 | PFD | 11 | N-0 PFD 11 | 80.9706 | 1.0059
[29 empty] | N-1 | EENS | 12 | N-1 EENS 12 | 1008.9296 | 0
[29 empty] | N-1 | IP | 12 | N-1 IP 12 | 100.1707 | 0
[29 empty] | N-1 | SAIDI | 12 | N-1 SAIDI 12 | 73.3366 | 0
[29 empty] | N-1 | SAIFI | 12 | N-1 SAIFI 12 | 1.4722 | 0
[29 empty] | N-1 | PFD | 12 | N-1 PFD 12 | 315.9581 | 0
[29 empty] | N-1 | Available Flex-1 | 12 | N-1 Available Flex-1 12 | 75415.3058 | 58290.7404
[29 empty] | N-1 | Available Flex-2-1 | 12 | N-1 Available Flex-2-1 12 | 1272587.0328 | 587520.0117
[29 empty] | N-1 | Available Flex-2-2 | 12 | N-1 Available Flex-2-2 12 | 526663.8571 | 167658.0135
[29 empty] | N-0 | EENS | 12 | N-0 EENS 12 | 3662.4319 | 0
[29 empty] | N-0 | IP | 12 | N-0 IP 12 | 603.3371 | 0
[29 empty] | N-0 | SAIDI | 12 | N-0 SAIDI 12 | 54.0898 | 0
[29 empty] | N-0 | SAIFI | 12 | N-0 SAIFI 12 | 2.9079 | 0
[29 empty] | N-0 | PFD | 12 | N-0 PFD 12 | 81.9765 | 0
[29 empty] | N-1 | EENS | 13 | N-1 EENS 13 | 114.4291 | 894.5005
[29 empty] | N-1 | IP | 13 | N-1 IP 13 | -30.4126 | 130.5833
[29 empty] | N-1 | SAIDI | 13 | N-1 SAIDI 13 | 54.4087 | 18.928
[29 empty] | N-1 | SAIFI | 13 | N-1 SAIFI 13 | 0.65104 | 0.82113
[29 empty] | N-1 | PFD | 13 | N-1 PFD 13 | 225.5303 | 90.4278
[29 empty] | N-1 | Available Flex-1 | 13 | N-1 Available Flex-1 13 | 39141.4455 | 94564.6006
[29 empty] | N-1 | Available Flex-2-1 | 13 | N-1 Available Flex-2-1 13 | 0 | 1860107.0445
[29 empty] | N-1 | Available Flex-2-2 | 13 | N-1 Available Flex-2-2 13 | 479183.4057 | 215138.4648
[29 empty] | N-0 | EENS | 13 | N-0 EENS 13 | 3422.1306 | 240.3013
[29 empty] | N-0 | IP | 13 | N-0 IP 13 | 527.3168 | 76.0203
[29 empty] | N-0 | SAIDI | 13 | N-0 SAIDI 13 | 49.0833 | 5.0065
[29 empty] | N-0 | SAIFI | 13 | N-0 SAIFI 13 | 2.6068 | 0.30108
[29 empty] | N-0 | PFD | 13 | N-0 PFD 13 | 73.8974 | 8.0791

## Incr. C-B Monetized
Incremental Cost-Benefit analysis taking into consideration applicable Monetized Benefits
# | Project | Present Value | Aggregate | [25 empty] | For Calculations only
0 | Baseline | 0 | 0 | [25 empty] | Category |  |  |  | NPV of benefits between Project and Baseline | NPV of Project Performance
6 | Valley South to Valley North and Distributed BESS in Valley South | 185 | 328 | [25 empty] | N-0 | EENS | 1 | N-0 EENS 1 | 135.9394 | 0
13 | Valley South to Valley North | 185.2 | 951 | [25 empty] | N-0 | Losses | 1 | N-0 Losses 1 | 4.507 | 0
10 | Valley South to Valley North and Centralized BESS in Valley South and Valley North | 239 | 540 | [25 empty] | N-1 | EENS | 1 | N-1 EENS 1 | 1.8201 | 0
3 | Valley South to Valley North to Vista | 270 | 538 | [25 empty] | N-1 | Flexibility-1 | 1 | N-1 Flexibility-1 1 | 3649.9667 | 0
11 | Valley South to Valley North to Vista and Centralized BESS in Valley South | 270 | 685 | [25 empty] | N-1 | Flexibility-2-1 | 1 | N-1 Flexibility-2-1 1 | 410.6179 | 0
8 | Mira Loma | 290 | 881 | [25 empty] | N-1 | Flexibility-2-2 | 1 | N-1 Flexibility-2-2 1 | 241.6393 | 0
7 | Menifee | 315 | 358 | [25 empty] | Total | Aggregate | 1 | Total Aggregate 1 | 4439.9833 | 0
4 | Centralized BESS in Valley South | 417 | 273 | [25 empty] | N-0 | EENS | 2 | N-0 EENS 2 | 135.9171 | 0
5 | Mira Loma and Centralized BESS in Valley South | 429 | 285 | [25 empty] | N-0 | Losses | 2 | N-0 Losses 2 | 3.1938 | 0
2 | SDG&E | 469 | 190 | [25 empty] | N-1 | EENS | 2 | N-1 EENS 2 | 1.8282 | 0
12 | SDG&E and Centralized BESS in Valley South | 504 | 545 | [25 empty] | N-1 | Flexibility-1 | 2 | N-1 Flexibility-1 2 | 1597.6488 | 0
1 | Alberhill System Project | 545 | 187 | [25 empty] | N-1 | Flexibility-2-1 | 2 | N-1 Flexibility-2-1 2 | 294.5223 | 0
9 | SCE Orange County | 806 | 1004 | [25 empty] | N-1 | Flexibility-2-2 | 2 | N-1 Flexibility-2-2 2 | 175.8511 | 0
[29 empty] | Total | Aggregate | 2 | Total Aggregate 2 | 2205.7675 | 0
[29 empty] | N-0 | EENS | 3 | N-0 EENS 3 | 135.1936 | 0
Present Value of Monetized Benefits($) | [28 empty] | N-0 | Losses | 3 | N-0 Losses 3 | 0.38717 | 0
|  | Alberhill System Project | SDG&E | Valley South to Valley North to Vista | Centralized BESS in Valley South | Mira Loma and Centralized BESS in Valley South | Valley South to Valley North and Distributed BESS in Valley South | Menifee | Mira Loma | SCE Orange County | Valley South to Valley North and Centralized BESS in Valley South and Valley North | Valley South to Valley North to Vista and Centralized BESS in Valley South | SDG&E and Centralized BESS in Valley South | Valley South to Valley North | [14 empty] | N-1 | EENS | 3 | N-1 EENS 3 | 0.17582 | 0
Category |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | [14 empty] | N-1 | Flexibility-1 | 3 | N-1 Flexibility-1 3 | 1061.616 | 0
N-0 | EENS ($M) | 135939350.8811 | 135917102.81 | 135193609.5469 | 135939350.8811 | 135939350.8811 | 124537997.1687 | 135939350.8811 | 117972011.6501 | 135939350.8811 | 135939350.8811 | 135193609.5469 | 135939350.8811 | 124537997.1687 | [14 empty] | N-1 | Flexibility-2-1 | 3 | N-1 Flexibility-2-1 3 | 0 | 0
N-0 | Losses ($M) | 4506963.013 | 3193830.838 | 387169.6632 | 806178.5419 | 782066.8229 | 387169.6632 | 614918.6288 | 771017.4899 | 3188562.7007 | 387169.6632 | 387169.6632 | 3043834.6939 | 387169.6632 | [14 empty] | N-1 | Flexibility-2-2 | 3 | N-1 Flexibility-2-2 3 | 158.8508 | 0
N-1 | EENS ($M) | 1820076.45 | 1828224.7753 | 175819.9607 | 1828224.7753 | 1369953.6223 | 175819.9607 | 128692.9756 | 576772.5246 | 1639421.6194 | 175819.9607 | 175819.9607 | 1828224.7753 | 175819.9607 | [14 empty] | Total | Aggregate | 3 | Total Aggregate 3 | 1355.8362 | 0
N-1 | Flexibility-1 ($M) | 3649966661.1871 | 1597648819.9312 | 1061615971.2793 | 2216490536.0483 | 2362810199.7121 | 1061615971.2793 | 1061615971.2793 | 2289858231.7733 | 3092624203.417 | 1061615971.2793 | 1061615971.2793 | 1956625091.4149 | 1061615971.2793 | [14 empty] | N-0 | EENS | 4 | N-0 EENS 4 | 135.9394 | 0
N-1 | Flexibility-2-1 ($M) | 410617949.0524 | 294522289.2355 | 0 | 342.7365 | 115622912.2425 | 0 | 262111066.8756 | 115622912.2425 | 300079046.6467 | 0 | 0 | 294522289.2355 | 0 | [14 empty] | N-0 | Losses | 4 | N-0 Losses 4 | 0.80618 | 0
N-1 | Flexibility-2-2 ($M) | 241639286.0361 | 175851094.6125 | 158850774.4516 | 1267956.9556 | 149022625.4435 | 158850774.4516 | 158850774.4516 | 149022625.4435 | 186936510.0182 | 158850774.4516 | 158850774.4516 | 175851094.6125 | 158850774.4516 | [14 empty] | N-1 | EENS | 4 | N-1 EENS 4 | 1.8282 | 0
Total | Aggregate ($M) | 4439.9833 | 2205.7675 | 1355.8362 | 2355.5264 | 2764.765 | 1345.1806 | 1618.6459 | 2673.0526 | 3717.2185 | 1356.5819 | 1355.8362 | 2564.7661 | 1345.1806 | [14 empty] | N-1 | Flexibility-1 | 4 | N-1 Flexibility-1 4 | 2216.4905 | 0
[29 empty] | N-1 | Flexibility-2-1 | 4 | N-1 Flexibility-2-1 4 | 0.00034274 | 0
[29 empty] | N-1 | Flexibility-2-2 | 4 | N-1 Flexibility-2-2 4 | 1.268 | 0
Ranking of Projects by Cost | [28 empty] | Total | Aggregate | 4 | Total Aggregate 4 | 2355.5264 | 0
[29 empty] | N-0 | EENS | 5 | N-0 EENS 5 | 135.9394 | 0
Category |  | 0 | 6 | 13 | 10 | 3 | 11 | 8 | 7 | 4 | 5 | 2 | 12 | 1 | 9 | [13 empty] | N-0 | Losses | 5 | N-0 Losses 5 | 0.78207 | 0
[29 empty] | N-1 | EENS | 5 | N-1 EENS 5 | 1.37 | 0
[29 empty] | N-1 | Flexibility-1 | 5 | N-1 Flexibility-1 5 | 2362.8102 | 0
Category |  | 1: Alternative selection | [13 empty] | Preferred Trend | N-1 | Flexibility-2-1 | 5 | N-1 Flexibility-2-1 5 | 115.6229 | 0
|  | 1: 0 --> 6; 3: 6 --> 13; 5: 6 --> 10; 7: 10 --> 3; 9: 10 --> 11; 11: 10 --> 8; 13: 8 --> 7 |  | 8 --> 4 |  | 8 --> 5 |  | 8 --> 2 |  | 8 --> 12 |  | 12 --> 1 |  | 1 --> 9 |  |  | N-1 | Flexibility-2-2 | 5 | N-1 Flexibility-2-2 5 | 149.0226 | 0
|  | 0 | 6 | 6 | 13 | 6 | 10 | 10 | 3 | 10 | 11 | 10 | 8 | 8 | 7 | 8 | 4 | 8 | 5 | 8 | 2 | 8 | 12 | 12 | 1 | 1 | 9 |  | Total | Aggregate | 5 | Total Aggregate 5 | 2764.765 | 0
N-0 | EENS | 1: 0.67318; 3: 0; 5: 0.21114; 7: -0.024056; 9: -0.024056; 11: -0.3523; 13: 0.71869 |  | 0.14148 |  | 0.12926 |  | 0.10025 |  | 0.08396 |  | 0 |  | 0 |  | ↑ | N-0 | EENS | 0 | N-0 EENS 0 | 0 | 0
N-0 | Losses | 1: 0.0020928; 3: 0; 5: 0; 7: 0; 9: 0; 11: 0.0075264; 13: -0.006244 |  | 0.00027686 |  | 7.9492e-05 |  | 0.013535 |  | 0.010621 |  | 0.035686 |  | -0.0050513 |  | ↑ | N-0 | Losses | 0 | N-0 Losses 0 | 0 | 0
N-1 | EENS | 1: 0.00095038; 3: 0; 5: 0; 7: 0; 9: 0; 11: 0.0078618; 13: -0.017923 |  | 0.009854 |  | 0.0057063 |  | 0.0069914 |  | 0.0058479 |  | -0.00019874 |  | -0.00069216 |  | ↑ | N-1 | EENS | 0 | N-1 EENS 0 | 0 | 0
N-1 | Flexibility-1 | 1: 5.7385; 3: 0; 5: 0; 7: 0; 9: 0; 11: 24.0832; 13: -49.1297 |  | -0.5777 |  | 0.52483 |  | -3.8671 |  | -1.5572 |  | 41.301 |  | -2.1354 |  | ↑ | N-1 | Flexibility-1 | 0 | N-1 Flexibility-1 0 | 0 | 0
N-1 | Flexibility-2-1 | 1: 0; 3: 0; 5: 0; 7: 0; 9: 0; 11: 2.2671; 13: 5.8595 |  | -0.91041 |  | 0 |  | 0.99944 |  | 0.83598 |  | 2.8316 |  | -0.42352 |  | ↑ | N-1 | Flexibility-2-1 | 0 | N-1 Flexibility-2-1 0 | 0 | 0
N-1 | Flexibility-2-2 | 1: 0.85865; 3: 0; 5: 0; 7: 0; 9: 0; 11: -0.19271; 13: 0.39313 |  | -1.1634 |  | 0 |  | 0.14988 |  | 0.12537 |  | 1.6046 |  | -0.20959 |  | ↑ | N-1 | Flexibility-2-2 | 0 | N-1 Flexibility-2-2 0 | 0 | 0
Total | Aggregate | 1: 7.2712; 3: 0; 5: 0.21114; 7: -0.024056; 9: -0.024056; 11: 25.8131; 13: -42.1763 |  | -2.5002 |  | 0.6598 |  | -2.6105 |  | -0.50601 |  | 45.737 |  | -2.7692 |  | ↑ | Total | Aggregate | 0 | Total Aggregate 0 | 0 | 0
Decision to move forward (Y/N) | [15 empty] | N |  | N |  | N |  | Y |  | Y |  | N |  |  | N-0 | EENS | 6 | N-0 EENS 6 | 124.538 | 0 | bar: 1; 3; 5; 7; 9; 11; 13
[29 empty] | N-0 | Losses | 6 | N-0 Losses 6 | 0.38717 | 0
[29 empty] | N-1 | EENS | 6 | N-1 EENS 6 | 0.17582 | 0
[29 empty] | N-1 | Flexibility-1 | 6 | N-1 Flexibility-1 6 | 1061.616 | 0
[29 empty] | N-1 | Flexibility-2-1 | 6 | N-1 Flexibility-2-1 6 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 6 | N-1 Flexibility-2-2 6 | 158.8508 | 0
[29 empty] | Total | Aggregate | 6 | Total Aggregate 6 | 1345.1806 | 0
[29 empty] | N-0 | EENS | 7 | N-0 EENS 7 | 135.9394 | 0
[29 empty] | N-0 | Losses | 7 | N-0 Losses 7 | 0.61492 | 0
[29 empty] | N-1 | EENS | 7 | N-1 EENS 7 | 0.12869 | 0
[29 empty] | N-1 | Flexibility-1 | 7 | N-1 Flexibility-1 7 | 1061.616 | 0
[29 empty] | N-1 | Flexibility-2-1 | 7 | N-1 Flexibility-2-1 7 | 262.1111 | 0
[29 empty] | N-1 | Flexibility-2-2 | 7 | N-1 Flexibility-2-2 7 | 158.8508 | 0
[29 empty] | Total | Aggregate | 7 | Total Aggregate 7 | 1618.6459 | 0
[29 empty] | N-0 | EENS | 8 | N-0 EENS 8 | 117.972 | 0
[29 empty] | N-0 | Losses | 8 | N-0 Losses 8 | 0.77102 | 0
[29 empty] | N-1 | EENS | 8 | N-1 EENS 8 | 0.57677 | 0
[29 empty] | N-1 | Flexibility-1 | 8 | N-1 Flexibility-1 8 | 2289.8582 | 0
[29 empty] | N-1 | Flexibility-2-1 | 8 | N-1 Flexibility-2-1 8 | 115.6229 | 0
[29 empty] | N-1 | Flexibility-2-2 | 8 | N-1 Flexibility-2-2 8 | 149.0226 | 0
[29 empty] | Total | Aggregate | 8 | Total Aggregate 8 | 2673.0526 | 0
[29 empty] | N-0 | EENS | 9 | N-0 EENS 9 | 135.9394 | 0
[29 empty] | N-0 | Losses | 9 | N-0 Losses 9 | 3.1886 | 0
[29 empty] | N-1 | EENS | 9 | N-1 EENS 9 | 1.6394 | 0
[29 empty] | N-1 | Flexibility-1 | 9 | N-1 Flexibility-1 9 | 3092.6242 | 0
[29 empty] | N-1 | Flexibility-2-1 | 9 | N-1 Flexibility-2-1 9 | 300.079 | 0
[29 empty] | N-1 | Flexibility-2-2 | 9 | N-1 Flexibility-2-2 9 | 186.9365 | 0
[29 empty] | Total | Aggregate | 9 | Total Aggregate 9 | 3717.2185 | 0
[29 empty] | N-0 | EENS | 10 | N-0 EENS 10 | 135.9394 | 0
[29 empty] | N-0 | Losses | 10 | N-0 Losses 10 | 0.38717 | 0
[29 empty] | N-1 | EENS | 10 | N-1 EENS 10 | 0.17582 | 0
[29 empty] | N-1 | Flexibility-1 | 10 | N-1 Flexibility-1 10 | 1061.616 | 0
[29 empty] | N-1 | Flexibility-2-1 | 10 | N-1 Flexibility-2-1 10 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 10 | N-1 Flexibility-2-2 10 | 158.8508 | 0
[29 empty] | Total | Aggregate | 10 | Total Aggregate 10 | 1356.5819 | 0
[29 empty] | N-0 | EENS | 11 | N-0 EENS 11 | 135.1936 | 0
[29 empty] | N-0 | Losses | 11 | N-0 Losses 11 | 0.38717 | 0
[29 empty] | N-1 | EENS | 11 | N-1 EENS 11 | 0.17582 | 0
[29 empty] | N-1 | Flexibility-1 | 11 | N-1 Flexibility-1 11 | 1061.616 | 0
[29 empty] | N-1 | Flexibility-2-1 | 11 | N-1 Flexibility-2-1 11 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 11 | N-1 Flexibility-2-2 11 | 158.8508 | 0
[29 empty] | Total | Aggregate | 11 | Total Aggregate 11 | 1355.8362 | 0
[29 empty] | N-0 | EENS | 12 | N-0 EENS 12 | 135.9394 | 0
[29 empty] | N-0 | Losses | 12 | N-0 Losses 12 | 3.0438 | 0
[29 empty] | N-1 | EENS | 12 | N-1 EENS 12 | 1.8282 | 0
[29 empty] | N-1 | Flexibility-1 | 12 | N-1 Flexibility-1 12 | 1956.6251 | 0
[29 empty] | N-1 | Flexibility-2-1 | 12 | N-1 Flexibility-2-1 12 | 294.5223 | 0
[29 empty] | N-1 | Flexibility-2-2 | 12 | N-1 Flexibility-2-2 12 | 175.8511 | 0
[29 empty] | Total | Aggregate | 12 | Total Aggregate 12 | 2564.7661 | 0
[29 empty] | N-0 | EENS | 13 | N-0 EENS 13 | 124.538 | 0
[29 empty] | N-0 | Losses | 13 | N-0 Losses 13 | 0.38717 | 0
[29 empty] | N-1 | EENS | 13 | N-1 EENS 13 | 0.17582 | 0
[29 empty] | N-1 | Flexibility-1 | 13 | N-1 Flexibility-1 13 | 1061.616 | 0
[29 empty] | N-1 | Flexibility-2-1 | 13 | N-1 Flexibility-2-1 13 | 0 | 0
[29 empty] | N-1 | Flexibility-2-2 | 13 | N-1 Flexibility-2-2 13 | 158.8508 | 0
[29 empty] | Total | Aggregate | 13 | Total Aggregate 13 | 1345.1806 | 0

## Levelized Cost Analysis
Evaluation of Present Value of Cost $/ Present Value of Benefit
Alternative Ranking
Levelized cost analysis ( Present Value of Cost $/Present Value of Benefit) for each Alternative
|  | Alberhill System Project | SDG&E | Valley South to Valley North to Vista | Centralized BESS in Valley South | Mira Loma and Centralized BESS in Valley South | Valley South to Valley North and Distributed BESS in Valley South | Menifee | Mira Loma | SCE Orange County | Valley South to Valley North and Centralized BESS in Valley South and Valley North | Valley South to Valley North to Vista and Centralized BESS in Valley South | SDG&E and Centralized BESS in Valley South | Valley South to Valley North
Reliability Metrics |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | Rank #1 | Rank #2 | Rank #3
N-1 | EENS ↓ | 0.54473 | 0.46485 | 2.3595 | 0.41331 | 0.56924 | 1.6167 | 2.7528 | 0.57572 | 0.96091 | 2.0886 | 2.3595 | 0.49954 | 1.6167 | 4 | 2 | 12
N-1 | IP ↓ | 5.6407 | 4.682 | 8.8779 | 4.1629 | 9.8243 | 6.083 | 10.3575 | 11.8029 | 10.0997 | 7.8586 | 8.8779 | 5.0314 | 6.083 | 4 | 2 | 12
N-1 | SAIDI ↓ | 7.4397 | 6.3952 | 4.9624 | 5.6861 | 6.2019 | 3.4002 | 5.7895 | 4.5145 | 11.2687 | 4.3927 | 4.9624 | 6.8724 | 3.4002 | 6 | 6 | 10
N-1 | SAIFI ↓ | 375.6448 | 318.5772 | 414.7181 | 283.2552 | 354.793 | 284.1587 | 483.8378 | 303.0368 | 624.9572 | 367.1023 | 414.7181 | 342.3516 | 284.1587 | 4 | 6 | 6
N-1 | PFD ↓ | 1.7352 | 1.4844 | 1.1972 | 1.3198 | 1.5937 | 0.82029 | 1.3967 | 1.0821 | 2.9659 | 1.0597 | 1.1972 | 1.5951 | 0.82029 | 6 | 6 | 10
N-1 | Flex-1↓ | 0.0040761 | 0.0077902 | 0.0068981 | 0.0050777 | 0.0050173 | 0.0047264 | 0.0080477 | 0.0034767 | 0.0071141 | 0.0061061 | 0.0068981 | 0.006683 | 0.0047264 | 8 | 1 | 6
N-1 | Flex-2-1↓ | 0.00030805 | 0.00036854 |  |  | 0.0008587 |  | 0.00027807 | 0.00058047 | 0.00062175 |  |  | 0.00039604 |  | 7 | 1 | 2
N-1 | Flex-2-2↓ | 0.00078494 | 0.00089051 | 0.00056346 | 0.12049 | 0.00095086 | 0.00038607 | 0.00065737 | 0.00064278 | 0.001447 | 0.00049877 | 0.00056346 | 0.00095697 | 0.00038607 | 6 | 6 | 10
N-0 | EENS ↓ | 0.14881 | 0.12806 | 0.073949 | 0.11386 | 0.11714 | 0.05406 | 0.086008 | 0.091853 | 0.22007 | 0.065257 | 0.073949 | 0.13761 | 0.05406 | 6 | 6 | 10
N-0 | IP ↓ | 0.90331 | 0.77764 | 0.45215 | 0.69116 | 0.71105 | 0.35083 | 0.5221 | 0.58717 | 1.3359 | 0.39613 | 0.45215 | 0.83535 | 0.35083 | 6 | 6 | 10
N-0 | SAIDI ↓ | 10.0758 | 8.6708 | 4.9962 | 7.7094 | 7.9313 | 3.7691 | 5.8236 | 7.6577 | 14.9011 | 4.4186 | 4.9962 | 9.3178 | 3.7691 | 6 | 6 | 10
N-0 | SAIFI ↓ | 187.4223 | 161.2974 | 93.1658 | 143.4039 | 147.5306 | 70.9685 | 108.3267 | 131.843 | 277.1787 | 82.1907 | 93.1658 | 173.3227 | 70.9685 | 6 | 6 | 10
N-0 | PFD ↓ | 6.6482 | 5.7265 | 3.3345 | 5.0868 | 5.2332 | 2.5035 | 3.8426 | 3.8808 | 9.8321 | 2.9155 | 3.3345 | 6.1481 | 2.5035 | 6 | 6 | 10
Count of Rank #1 |  | 0 | 0 | 0 | 3 | 0 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 0

## Cost Assumptions
Financial and Study Parameters | Value | Unit | Source
Discount Rate (Weighted Aggregate Cost of Capital) | 10% |  | CPUC
Customer price (Average Locational Marginal Price in Valley South - 2022) | 40 | $/MWh | CAISO
Inflation Rate | 1.025 |  | Quanta
Load distribution : Residential | 90% |  | SCE
Load distribution : Commercial | 10% |  | SCE
Customer Interruption cost for Flex-1 events (6hours) : N-1 : Residential | 4.1725 | $/kWh | LBNL
Customer Interruption cost (Average cost over 24 hr duration) : N-0 : Residential (Flex-2 Component 1) | 3.5213 | $/kWh | LBNL
Customer Interruption cost for Flex-1 events (6hours) : N-1 : Commercial | 154.7025 | $/kWh | LBNL
Customer Interruption cost (Average cost over 24 hr duration) : N-0 : Residential (Flex-2 Component 1) | 142.8531 | $/kWh | LBNL
Annual Outage rate for Transformer N-2 Outage events | 0.0169 |  | NERC
Annual Outage rate for High Impact Low Probability(HILP) Events | 0.01 |  | NERC
Flex-1 Duration of evaluation | 1 | hour | Quanta
Normalization Factor for Cost Benefit | 1 |  | Quanta

## Baseline System Analysis
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
Valley South (alone) | Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential | Cost of Reliability (N-2) | $/kwh | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Commerical | Cost of Reliability (N-2) | $/kwh | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Residential (N-1) | Monetized EENS | 355030.5479 | 1354.9655 | 3468.8297 | 5582.694 | 7696.5582 | 9810.4224 | 11924.2866 | 14038.1508 | 12087.1452 | 10461.5877 | 8610.5229 | 12532.4529 | 19218.8075 | 25905.162 | 32591.5165 | 39277.8711 | 45964.2256 | 52650.5801 | 81297.3831 | 109944.1861 | 138590.9891 | 167237.792 | 195884.595 | 242156.0727 | 288427.5504 | 334699.0281 | 380970.5058 | 427241.9834
Commerical(N-1) | Monetized EENS | 1473194.2274 | 5622.4102 | 14393.8598 | 23165.3095 | 31936.7591 | 40708.2087 | 49479.6583 | 58251.108 | 50155.4378 | 43410.21 | 35729.2429 | 52003.2359 | 79748.1693 | 107493.1026 | 135238.036 | 162982.9694 | 190727.9028 | 218472.8361 | 337342.3391 | 456211.8421 | 575081.3451 | 693950.8481 | 812820.3511 | 1004823.1921 | 1196826.033 | 1388828.8739 | 1580831.7149 | 1772834.5558
Aggregate | Monetized EENS | 1828224.7753 | 6977.3757 | 17862.6896 | 28748.0034 | 39633.3173 | 50518.6311 | 61403.9449 | 72289.2588 | 62242.583 | 53871.7977 | 44339.7658 | 64535.6888 | 98966.9767 | 133398.2646 | 167829.5525 | 202260.8405 | 236692.1284 | 271123.4163 | 418639.7222 | 566156.0282 | 713672.3342 | 861188.6402 | 1008704.9462 | 1246979.2648 | 1485253.5834 | 1723527.902 | 1961802.2206 | 2200076.5392
Residential (N-0) | Monetized EENS | 24322736.8672 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21673528.3995
Commerical(N-0) | Monetized EENS | 111616614.0139 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98364469.7349
Aggregate | Monetized EENS | 135939350.8811 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 120037998.1344
Residential (N-1) | Monetized Value for Flex-1 | 712935284.0978 | 22022883.7382 | 30015837.815 | 38394675.2933 | 47173694.7469 | 56367668.5011 | 65991857.3838 | 76062025.9178 | 75086616.0985 | 74014897.0219 | 68308752.9701 | 74663729.4279 | 89742796.9937 | 96979854.661 | 104522675.9637 | 112382025.9222 | 120569016.7063 | 129095118.2633 | 137972169.2628 | 147212388.3633 | 156828385.813 | 166833175.3925 | 177240186.7098 | 188063277.8584 | 199316748.4477 | 211015353.0179 | 223174314.8487 | 235809340.1755
Commerical(N-1) | Monetized Value for Flex-1 | 2937031377.0893 | 90726187.9104 | 123654221.4119 | 158171952.7211 | 194338286.7074 | 232214079.9225 | 271862201.3692 | 313347595.0882 | 309329265.0815 | 304914176.3274 | 281406959.7591 | 307587127.4036 | 369707344.4355 | 399521362.5112 | 430595014.4003 | 462972648.0324 | 496700041.462 | 531824446.6581 | 568394634.5881 | 606460941.6355 | 646075317.3886 | 687291373.8408 | 730164436.0423 | 774751594.2452 | 821111757.5857 | 869305709.3468 | 919396163.8475 | 971447825.0049
Aggregate | Monetized Value for Flex-1 | 3649966661.1871 | 112749071.6485 | 153670059.2269 | 196566628.0144 | 241511981.4542 | 288581748.4236 | 337854058.753 | 389409621.0061 | 384415881.1799 | 378929073.3493 | 349715712.7291 | 382250856.8315 | 459450141.4292 | 496501217.1722 | 535117690.364 | 575354673.9546 | 617269058.1683 | 660919564.9215 | 706366803.8509 | 753673329.9987 | 802903703.2016 | 854124549.2333 | 907404622.7521 | 962814872.1036 | 1020428506.0334 | 1080321062.3647 | 1142570478.6962 | 1207257165.1804
Residential | Monetized Value for Flex-2_1 | 78487372.1953 | 6582087.2606 | 6829704.9761 | 7040875.7898 | 7259479.0789 | 7486869.9132 | 7727984.1793 | 7976465.26 | 8138521.7348 | 8303698.6399 | 8472040.5509 | 8748283.9452 | 9034868.2791 | 9332332.1551 | 9637667.5155 | 9954039.3859 | 10281604.5477 | 10621208.842 | 10963694.7849 | 11317020.5303 | 11681132.361 | 12056910.3256 | 12429963.6743 | 12812401.9662 | 13203740.6434 | 13604639.829 | 13996554.1009 | 14393913.6756
Commerical | Monetized Value for Flex-2_1 | 353793756.672 | 29669758.5044 | 30785932.9837 | 31737817.5145 | 32723205.0579 | 33748203.7968 | 34835062.9894 | 35955129.2184 | 36685623.404 | 37430183.4029 | 38189010.1469 | 39434219.2231 | 40726041.6562 | 42066905.2782 | 43443250.8119 | 44869345.092 | 46345894.8338 | 47876712.7949 | 49420520.2246 | 51013189.7114 | 52654479.1169 | 54348355.3933 | 56029950.0495 | 57753848.7634 | 59517867.3169 | 61324981.3141 | 63091594.4478 | 64882753.1115
Aggregate | Monetized Value for Flex-2_1 | 432281128.8673 | 36251845.765 | 37615637.9598 | 38778693.3042 | 39982684.1368 | 41235073.7101 | 42563047.1687 | 43931594.4784 | 44824145.1388 | 45733882.0428 | 46661050.6978 | 48182503.1683 | 49760909.9353 | 51399237.4334 | 53080918.3274 | 54823384.4778 | 56627499.3815 | 58497921.6369 | 60384215.0095 | 62330210.2417 | 64335611.478 | 66405265.7189 | 68459913.7238 | 70566250.7296 | 72721607.9603 | 74929621.1431 | 77088148.5487 | 79276666.7872
Residential | Monetized Value for Flex-2_2 | 47838978.0819 | 3183499.0202 | 3501307.5196 | 3708829.3817 | 3936509.7003 | 4165527.9382 | 4437750.1701 | 4723555.5232 | 4727091.2557 | 4720976.8394 | 4717667.3258 | 5037991.8476 | 5376063.1092 | 5736272.6748 | 6122929.789 | 6538124.8089 | 6936168.5746 | 7366992.5845 | 7818517.6191 | 8280089.6569 | 8778377.424 | 9286584.5831 | 9782273.8356 | 10321652.155 | 10821977.1332 | 11349087.8904 | 11822570.2093 | 12285127.6815
Commerical | Monetized Value for Flex-2_2 | 193800307.9542 | 12889019.006 | 14192477.1172 | 15032700.6183 | 15976287.3164 | 16895734.6492 | 17993941.9531 | 19143523.3426 | 19173348.3887 | 19152910.7452 | 19135985.3705 | 20429948.5115 | 21793565.667 | 23254111.2204 | 24802464.1462 | 26485157.7194 | 28054321.3829 | 29785320.2104 | 31601293.7538 | 33493387.8942 | 35525977.2878 | 37550540.8887 | 39560369.5036 | 41749420.1024 | 43788085.1699 | 45912774.4336 | 47813600.8056 | 49658023.6514
Aggregate | Monetized Value for Flex-2_2 | 241639286.0361 | 16072518.0262 | 17693784.6368 | 18741530 | 19912797.0167 | 21061262.5875 | 22431692.1232 | 23867078.8658 | 23900439.6443 | 23873887.5846 | 23853652.6963 | 25467940.3591 | 27169628.7762 | 28990383.8952 | 30925393.9352 | 33023282.5284 | 34990489.9575 | 37152312.7949 | 39419811.3728 | 41773477.5511 | 44304354.7117 | 46837125.4718 | 49342643.3392 | 52071072.2574 | 54610062.3031 | 57261862.3239 | 59636171.0148 | 61943151.3329
Aggregate Monetized Costs ($) |  | 4461654651.7469 | 166144070.7602 | 211677406.1281 | 258048915.1583 | 306728285.9626 | 357580338.1117 | 409519999.2986 | 466391527.0687 | 460963046.366 | 455119147.5215 | 427955103.0582 | 463538820.1944 | 547220258.253 | 590862235.627 | 634888060.8692 | 680215157.3816 | 730189117.3446 | 783013758.9561 | 836452275.5143 | 894920875.9963 | 955031365.4653 | 1020255911.1935 | 1088161918.2261 | 1159211472.3446 | 1234009157.5375 | 1311541380.0836 | 1390168612.6963 | 1470715057.9741
Residential (N-1) | Monetized EENS | 355030.5479
Commerical(N-1) | Monetized EENS | 1473194.2274
Aggregate | Monetized EENS | 1828224.7753
Residential (N-0) | Monetized EENS | 24322736.8672
Commerical(N-0) | Monetized EENS | 111616614.0139
Aggregate | Monetized EENS | 135939350.8811
Residential (N-0) | Monetized Value for Flex-1 | 712935284.0978
Commerical(N-0) | Monetized Value for Flex-1 | 2937031377.0893
Aggregate | Monetized Value for Flex-1 | 3649966661.1871
Residential | Monetized Value for Flex-2 | 126326350.2771
Commerical | Monetized Value for Flex-3 | 547594064.6263
Aggregate | Monetized Value for Flex-4 | 673920414.9034
Aggregate ($M) |  | 4461.6547
Note on C3: Sum of the EENS accumulated under N-1 condition, considering all outages in the system
Note on C4: Representative of the peak MW load drop required while considering all outages
Note on C5: Sum of total customers interrupted for all outages x number of outage hours/ total number of customers served.
Note on C6: Sum of total hours customers were without power due to all outages/ total number of customers served.
Note on C7: Periods with flexibility shortages in the system
Note on C8: Sum of EENS accumulated due to N-0 overloads in the system (transformer and lines)
Note on C13: Sum of EENS accumulated under N-2 events in the systems (emergency, planned or unplanned maintainence events)
Note on C14: Sum of EENS accumulated under entire Valley substation outage (considered over 2 week period)
Note on C15: Sum of EENS accumulated considering N-2 transformer outage event at Valley South (Loss of Valley Transformer and unavailable spare)

## Alberhill System Project
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Alberhill System Project | Losses (MWh) | 40620.8118 | 40962.5566 | 41304.3014 | 41646.0462 | 41987.791 | 42329.5357 | 42671.2805 | 42107.2941 | 41919.9412 | 41744.1176 | 42027.09 | 42310.0623 | 42593.0346 | 42876.0069 | 43158.9792 | 43441.9516 | 43724.9239 | 44007.8962 | 44290.8685 | 44573.8408 | 44856.8131 | 45139.7855 | 45422.7578 | 45705.7301 | 45988.7024 | 46271.6747 | 46554.6471
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 9.52 | 12.54 | 15.56 | 18.58 | 30.2
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 4.68 | 5.66 | 6.64 | 7.62 | 9.8
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032883 | 0.071078 | 0.10927 | 0.14747 | 0.18566 | 0.38195
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016441 | 0.02408 | 0.031719 | 0.039358 | 0.046997 | 0.076389
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2.5 | 3 | 3.5 | 4 | 5
N-1 |  | Deficit Flex-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | Deficit Flex-2-1 | 7809.8904 | 8335.6702 | 8589.7918 | 8855.5672 | 9142.7332 | 9476.0126 | 9813.7007 | 9590.9187 | 9369.305 | 9150.1268 | 9502.2602 | 9868.9942 | 10251.0309 | 10642.1298 | 11047.0078 | 11462.2818 | 11892.5661 | 12291.2433 | 12698.9434 | 13109.7474 | 13525.782 | 13875.5217 | 14220.4424 | 14560.3321 | 14893.9839 | 15134.8604 | 15352.045
N-1 |  | Deficit Flex-2-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1482.8582 | 2025.1456 | 2567.4329 | 3109.7203 | 3652.0076 | 4194.295
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6153.0992 | 8403.3129 | 10653.5266 | 12903.7402 | 15153.9539 | 17404.1676
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 90790.1938 | Losses (MWh) | 9046.1882 | 9141.2338 | 9236.2794 | 9331.325 | 9426.3706 | 9521.4162 | 9616.4618 | 9590.8905 | 10068.4127 | 10534.4054 | 10541.6023 | 10548.7993 | 10555.9962 | 10563.1931 | 10570.39 | 10577.5869 | 10584.7838 | 10591.9807 | 10599.1776 | 10606.3746 | 10613.5715 | 10620.7684 | 10627.9653 | 10635.1622 | 10642.3591 | 10649.556 | 10656.7529
| 4506963.013 | Losses ($) | 361847.5294 | 374790.5868 | 388154.6423 | 401952.6565 | 416197.9747 | 430904.3384 | 446085.8966 | 456022.196 | 490695.3268 | 526241.1541 | 539765.6892 | 553637.5503 | 567865.651 | 582459.1332 | 597427.3734 | 612779.9888 | 628526.8428 | 644678.052 | 661243.9924 | 678235.306 | 695662.9078 | 713537.9926 | 731872.0424 | 750676.8334 | 769964.4439 | 789747.262 | 810037.9931
N-1 | 1000.4962 | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 447.2 | 514.48 | 581.76 | 649.04 | 716.32 | 775
N-1 | 96.6191 | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 25.6 | 25.8 | 26 | 26.2 | 26.4 | 25.4
N-1 | 73.2552 | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.3806 | 80.9911 | 68.6017 | 56.2122 | 43.8227 | 31.2752
N-1 | 1.4508 | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.396 | 1.2469 | 1.0979 | 0.94889 | 0.79986 | 0.62908
N-1 | 314.0886 | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 77 | 79.5 | 82 | 84.5 | 87 | 89
N-1 | 133706.0462 | Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 | 1769189.9238 | Flex-2-1 | 185054.7758 | 186903.5718 | 187776.9737 | 188669.8084 | 189601.1907 | 190664.9258 | 191724.0095 | 191025.9762 | 190326.8443 | 189625.1064 | 190748.0747 | 191897.1713 | 193074.9319 | 194214.8303 | 195374.1805 | 196551.4233 | 197750.8059 | 198834.0469 | 199914.9112 | 200992.1603 | 202073.722 | 202973.6266 | 203848.8684 | 204688.4125 | 205501.8159 | 206079.6072 | 206594.009
N-1 | 694321.8706 | Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
N-0 | 3662.4319 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 | 603.3371 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 | 54.0898 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 | 2.9079 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 | 81.9765 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 353448.1908 | 1354.9655 | 3468.8297 | 5582.694 | 7696.5582 | 9810.4224 | 11924.2866 | 14038.1508 | 12087.1452 | 10461.5877 | 8610.5229 | 12532.4529 | 19218.8075 | 25905.162 | 32591.5165 | 39277.8711 | 45964.2256 | 52650.5801 | 81297.3831 | 109944.1861 | 138590.9891 | 167237.792 | 194401.7368 | 240130.9271 | 285860.1175 | 331589.3078 | 377318.4981 | 423047.6885
Commerical(N-1) | EENS | 1466628.2592 | 5622.4102 | 14393.8598 | 23165.3095 | 31936.7591 | 40708.2087 | 49479.6583 | 58251.108 | 50155.4378 | 43410.21 | 35729.2429 | 52003.2359 | 79748.1693 | 107493.1026 | 135238.036 | 162982.9694 | 190727.9028 | 218472.8361 | 337342.3391 | 456211.8421 | 575081.3451 | 693950.8481 | 806667.2519 | 996419.8792 | 1186172.5064 | 1375925.1337 | 1565677.761 | 1755430.3882
Aggregate | EENS | 1820076.45 | 6977.3757 | 17862.6896 | 28748.0034 | 39633.3173 | 50518.6311 | 61403.9449 | 72289.2588 | 62242.583 | 53871.7977 | 44339.7658 | 64535.6888 | 98966.9767 | 133398.2646 | 167829.5525 | 202260.8405 | 236692.1284 | 271123.4163 | 418639.7222 | 566156.0282 | 713672.3342 | 861188.6402 | 1001068.9887 | 1236550.8063 | 1472032.6239 | 1707514.4415 | 1942996.2591 | 2178478.0767
Residential (N-0) | EENS | 24322736.8672 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21673528.3995
Commerical(N-0) | EENS | 111616614.0139 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98364469.7349
Aggregate | EENS | 135939350.8811 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 120037998.1344
Residential (N-1) | Value for Flex-1 | 712935284.0978 | 22022883.7382 | 30015837.815 | 38394675.2933 | 47173694.7469 | 56367668.5011 | 65991857.3838 | 76062025.9178 | 75086616.0985 | 74014897.0219 | 68308752.9701 | 74663729.4279 | 89742796.9937 | 96979854.661 | 104522675.9637 | 112382025.9222 | 120569016.7063 | 129095118.2633 | 137972169.2628 | 147212388.3633 | 156828385.813 | 166833175.3925 | 177240186.7098 | 188063277.8584 | 199316748.4477 | 211015353.0179 | 223174314.8487 | 235809340.1755
Commerical(N-1) | Value for Flex-1 | 2937031377.0893 | 90726187.9104 | 123654221.4119 | 158171952.7211 | 194338286.7074 | 232214079.9225 | 271862201.3692 | 313347595.0882 | 309329265.0815 | 304914176.3274 | 281406959.7591 | 307587127.4036 | 369707344.4355 | 399521362.5112 | 430595014.4003 | 462972648.0324 | 496700041.462 | 531824446.6581 | 568394634.5881 | 606460941.6355 | 646075317.3886 | 687291373.8408 | 730164436.0423 | 774751594.2452 | 821111757.5857 | 869305709.3468 | 919396163.8475 | 971447825.0049
Aggregate | Value for Flex-1 | 3649966661.1871 | 112749071.6485 | 153670059.2269 | 196566628.0144 | 241511981.4542 | 288581748.4236 | 337854058.753 | 389409621.0061 | 384415881.1799 | 378929073.3493 | 349715712.7291 | 382250856.8315 | 459450141.4292 | 496501217.1722 | 535117690.364 | 575354673.9546 | 617269058.1683 | 660919564.9215 | 706366803.8509 | 753673329.9987 | 802903703.2016 | 854124549.2333 | 907404622.7521 | 962814872.1036 | 1020428506.0334 | 1080321062.3647 | 1142570478.6962 | 1207257165.1804
Residential (N-1) | Value for Flex-2-1 | 74554084.4722 | 6315551.2423 | 6538113.1445 | 6732882.4446 | 6934018.0868 | 7142454.5839 | 7362089.6443 | 7588058.332 | 7749442.3392 | 7914107.3257 | 8082051.0941 | 8333161.1903 | 8592945.509 | 8861826.4509 | 9136999.591 | 9421330.746 | 9715052.222 | 10018693.1196 | 10325412.9397 | 10641080.5558 | 10965880.935 | 11300511.8304 | 11634607.8628 | 11976896.8509 | 12326878.843 | 12685260.753 | 13038949.9518 | 13398284.3035
Commerical(N-1) | Value for Flex-2-1 | 336063864.5801 | 28468306.9003 | 29471538.494 | 30349490.7102 | 31256140.1809 | 32195699.3645 | 33185737.7735 | 34204325.9703 | 34931788.9056 | 35674041.3538 | 36431073.4101 | 37562990.326 | 38734007.6177 | 39946029.3208 | 41186414.0636 | 42468079.9502 | 43792074.1358 | 45160781.6213 | 46543367.8178 | 47966287.5644 | 49430374.6284 | 50938774.2383 | 52444762.8712 | 53987682.4978 | 55565279.5085 | 57180740.4252 | 58775048.2335 | 60394802.4264
Aggregate of Flex-2 (Component 1) | Value for Flex-2-1 | 410617949.0524 | 34783858.1426 | 36009651.6385 | 37082373.1548 | 38190158.2677 | 39338153.9484 | 40547827.4178 | 41792384.3023 | 42681231.2448 | 43588148.6795 | 44513124.5043 | 45896151.5163 | 47326953.1268 | 48807855.7717 | 50323413.6546 | 51889410.6962 | 53507126.3579 | 55179474.7409 | 56868780.7575 | 58607368.1202 | 60396255.5634 | 62239286.0687 | 64079370.734 | 65964579.3487 | 67892158.3515 | 69866001.1781 | 71813998.1853 | 73793086.73
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 241639286.0361 | 16072518.0262 | 17693784.6368 | 18741530 | 19912797.0167 | 21061262.5875 | 22431692.1232 | 23867078.8658 | 23900439.6443 | 23873887.5846 | 23853652.6963 | 25467940.3591 | 27169628.7762 | 28990383.8952 | 30925393.9352 | 33023282.5284 | 34990489.9575 | 37152312.7949 | 39419811.3728 | 41773477.5511 | 44304354.7117 | 46837125.4718 | 49342643.3392 | 52071072.2574 | 54610062.3031 | 57261862.3239 | 59636171.0148 | 61943151.3329
Aggregate ($M) |  | 4439.9833 | 164676083.1378 | 210071419.8068 | 256352595.0088 | 304935760.0934 | 355683418.35 | 407504779.5477 | 464252316.8927 | 458820132.4719 | 452973414.1582 | 425807176.8646 | 461252468.5425 | 544786301.4444 | 588270853.9653 | 632130556.1964 | 677281183.6 | 727068744.321 | 779695312.0601 | 832936841.2623 | 891198033.8747 | 951092009.5507 | 1016089931.5434 | 1083773739.2788 | 1154599372.5052 | 1229166486.9691 | 1306461746.6582 | 1384875656.3713 | 1465209879.4544
Aggregate ($M)+ Monetized Losses |  | 4444.4903 | 165037930.6672 | 210446210.3935 | 256740749.6511 | 305337712.7499 | 356099616.3247 | 407935683.8861 | 464698402.7893 | 459276154.6679 | 453464109.485 | 426333418.0187 | 461792234.2317 | 545339938.9947 | 588838719.6163 | 632713015.3295 | 677878610.9734 | 727681524.3098 | 780323838.9029 | 833581519.3143 | 891859277.8671 | 951770244.8567 | 1016785594.4512 | 1084487277.2715 | 1155331244.5476 | 1229917163.8025 | 1307231711.1021 | 1385665403.6333 | 1466019917.4475
Project Cost |  | 545
Benefit-Cost Ratio |  | 8.155

## SDG&E
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| SDG&E | Losses (MWh) | 43917.34 | 44144.4625 | 44371.585 | 44598.7075 | 44825.83 | 45052.9525 | 45280.075 | 45135.34 | 44990.69 | 44840.08 | 45077.67 | 45309.8843 | 45542.0985 | 45774.3128 | 46006.5271 | 46238.7414 | 46470.9556 | 46703.1699 | 46935.3842 | 47167.5985 | 47399.8127 | 47632.027 | 47864.2413 | 48096.4555 | 48328.6698 | 48560.8841 | 48793.0984
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | Deficit Flex-1 | 1680.298 | 2876.7738 | 4073.2495 | 5269.7252 | 6466.2009 | 7662.6766 | 8859.1523 | 8453.4404 | 8047.7285 | 7642.0166 | 7844.8725 | 9531.5857 | 10245.3391 | 10959.0925 | 11672.8459 | 12386.5993 | 13100.3528 | 13814.1062 | 14527.8596 | 15241.613 | 15955.3664 | 16669.1199 | 17382.8733 | 18096.6267 | 18810.3801 | 19524.1335 | 20237.887
N-1 |  | Deficit Flex-2-1 | 57103.9364 | 58857.6368 | 59699.6043 | 60571.995 | 61496.8629 | 62558.6521 | 63631.2349 | 62922.9382 | 62220.1254 | 61520.6663 | 62642.0385 | 63807.6263 | 65017.0585 | 66209.8025 | 67437.5589 | 68700.8853 | 70007.3228 | 71205.5074 | 72422.1093 | 73645.384 | 74886.792 | 75927.3849 | 76947.7251 | 77938.9668 | 78904.9135 | 79596.3231 | 80217.6368
|  | Deficit Flex-2-2 | 12005.7424 | 13453.7958 | 14178.8955 | 14937.2899 | 15757.2593 | 16749.9297 | 17791.8608 | 17102.1785 | 16427.9266 | 15778.9354 | 16830.1823 | 17964.2326 | 19172.9939 | 20408.244 | 21719.8418 | 23098.2324 | 24567.0678 | 25931.8136 | 27355.4567 | 28834.2072 | 30356.2803 | 31653.1061 | 32946.7014 | 34221.3621 | 35477.9187 | 36390.7641 | 37223.1347
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026075
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026075
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41772.4649
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249899.6174
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 3761250.6801 | 4284487.0478 | 4606811.8682 | 4995927.6228 | 5329720.0618 | 5796906.5792 | 6339283.6768 | 6199636.4515 | 6137390.4038 | 6039759.2997 | 6578075.4012 | 7231916.6265 | 7805029.2317 | 8551105.2609 | 9288340.8959 | 9994730.9369 | 10926172.2355 | 11789094.5164 | 12593607.0376 | 13521454.1614 | 14574371.2875 | 15540641.0811 | 16596015.8778 | 17613528.7795 | 18605991.6249 | 19459357.5512 | 20370726.3635
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 63772.9082 | Losses (MWh) | 5749.66 | 5959.3279 | 6168.9958 | 6378.6637 | 6588.3315 | 6797.9994 | 7007.6673 | 6562.8446 | 6997.6638 | 7438.4431 | 7491.0223 | 7548.9773 | 7606.9322 | 7664.8872 | 7722.8421 | 7780.7971 | 7838.7521 | 7896.707 | 7954.662 | 8012.6169 | 8070.5719 | 8128.5268 | 8186.4818 | 8244.4368 | 8302.3917 | 8360.3467 | 8418.3016
| 3193830.838 | Losses ($) | 229986.4 | 244332.4433 | 259252.0472 | 274764.9236 | 290891.4112 | 307652.4951 | 325069.8262 | 312046.3959 | 341038.9562 | 371583.8445 | 383565.6751 | 396196.494 | 409219.1254 | 422645.2655 | 436486.9507 | 450756.5668 | 465466.8594 | 480630.9438 | 496262.3156 | 512374.8617 | 528982.8711 | 546101.0467 | 563744.5168 | 581928.8472 | 600670.0538 | 619984.6153 | 639889.486
N-1 | 1008.9296 | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 | 100.1707 | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 | 73.3366 | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 | 1.4722 | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 | 315.9581 | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-1 | 60203.8892 | Flex-1 | 3765.5276 | 4364.5198 | 4963.512 | 5562.5041 | 6161.4963 | 6760.4884 | 7359.4806 | 7166.7032 | 6973.9259 | 5883.4146 | 6578.2925 | 7381.6473 | 7586.0302 | 7790.413 | 7994.7959 | 8199.1788 | 8403.5616 | 8607.9445 | 8812.3274 | 9016.7102 | 9221.0931 | 9425.476 | 9629.8588 | 9834.2417 | 10038.6246 | 10243.0075 | 10447.3903
N-1 | 1272587.0328 | Flex-2-1 | 135760.7298 | 136381.6052 | 136667.1611 | 136953.3806 | 137247.061 | 137582.2863 | 137906.4754 | 137693.9567 | 137476.0239 | 137254.5669 | 137608.2964 | 137958.5392 | 138308.9043 | 138647.1577 | 138983.6294 | 139312.8198 | 139636.0492 | 139919.7828 | 140191.7452 | 140456.5237 | 140712.712 | 140921.7634 | 141121.5858 | 141309.7778 | 141490.8863 | 141618.1445 | 141728.4172
N-2 | 526663.8571 | Flex-2-2 | 45808.4214 | 48737.9511 | 50182.2097 | 51691.2111 | 53310.9675 | 55169.0313 | 57028.8184 | 55797.1037 | 54578.426 | 53352.6808 | 55313.5827 | 57337.6933 | 59456.6336 | 61542.8136 | 63663.5828 | 65847.7387 | 68109.8281 | 70213.9163 | 72345.4015 | 74506.0026 | 76709.2379 | 78584.5378 | 80408.9696 | 82173.4363 | 83916.0273 | 85162.031 | 86278.2324
N-0 | 3662.2031 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2656.4
N-0 | 603.1082 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 196.2
N-0 | 54.0896 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6437
N-0 | 2.9077 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7446
N-0 | 81.9002 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 36
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 355030.5479 | 1354.9655 | 3468.8297 | 5582.694 | 7696.5582 | 9810.4224 | 11924.2866 | 14038.1508 | 12087.1452 | 10461.5877 | 8610.5229 | 12532.4529 | 19218.8075 | 25905.162 | 32591.5165 | 39277.8711 | 45964.2256 | 52650.5801 | 81297.3831 | 109944.1861 | 138590.9891 | 167237.792 | 195884.595 | 242156.0727 | 288427.5504 | 334699.0281 | 380970.5058 | 427241.9834
Commerical(N-1) | EENS | 1473194.2274 | 5622.4102 | 14393.8598 | 23165.3095 | 31936.7591 | 40708.2087 | 49479.6583 | 58251.108 | 50155.4378 | 43410.21 | 35729.2429 | 52003.2359 | 79748.1693 | 107493.1026 | 135238.036 | 162982.9694 | 190727.9028 | 218472.8361 | 337342.3391 | 456211.8421 | 575081.3451 | 693950.8481 | 812820.3511 | 1004823.1921 | 1196826.033 | 1388828.8739 | 1580831.7149 | 1772834.5558
Aggregate | EENS | 1828224.7753 | 6977.3757 | 17862.6896 | 28748.0034 | 39633.3173 | 50518.6311 | 61403.9449 | 72289.2588 | 62242.583 | 53871.7977 | 44339.7658 | 64535.6888 | 98966.9767 | 133398.2646 | 167829.5525 | 202260.8405 | 236692.1284 | 271123.4163 | 418639.7222 | 566156.0282 | 713672.3342 | 861188.6402 | 1008704.9462 | 1246979.2648 | 1485253.5834 | 1723527.902 | 1961802.2206 | 2200076.5392
Residential (N-0) | EENS | 24319550.5603 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21631755.9346
Commerical(N-0) | EENS | 111597552.2497 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98114570.1175
Aggregate | EENS | 135917102.81 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 119746326.0522
Residential (N-1) | Value for Flex-1 | 312063183.3267 | 15227769.3328 | 18091342.0026 | 21088575.9501 | 24224364.5062 | 27503762.1302 | 30931989.4075 | 34514438.1974 | 34450611.1087 | 34362021.1418 | 29713560.1581 | 34053541.751 | 39167536.831 | 41258306.7903 | 43429135.5371 | 45682719.2795 | 48021838.9993 | 50449363.0056 | 52968249.5627 | 55581549.5959 | 58292409.4747 | 61104073.879 | 64019888.7476 | 67043304.3134 | 70177878.2271 | 73427278.7712 | 76795288.1687 | 80285805.9868
Commerical(N-1) | Value for Flex-1 | 1285585636.6046 | 62732813.6664 | 74529680.7446 | 86877183.1682 | 99795479.6625 | 113305392.742 | 127428429.3008 | 142186801.817 | 141923857.6673 | 141558899.559 | 122408948.5483 | 140288077.8306 | 161355858.2411 | 169969062.1459 | 178912078.8346 | 188196015.6938 | 197832329.3467 | 207832836.1725 | 218209723.1338 | 228975558.9204 | 240143305.4195 | 251726329.5192 | 263738415.258 | 276193776.3277 | 289107068.9415 | 302493405.0757 | 316368366.0985 | 330748016.7943
Aggregate | Value for Flex-1 | 1597648819.9312 | 77960582.9992 | 92621022.7472 | 107965759.1183 | 124019844.1687 | 140809154.8722 | 158360418.7083 | 176701240.0144 | 176374468.776 | 175920920.7007 | 152122508.7064 | 174341619.5817 | 200523395.0721 | 211227368.9362 | 222341214.3717 | 233878734.9733 | 245854168.3461 | 258282199.1781 | 271177972.6965 | 284557108.5163 | 298435714.8942 | 312830403.3982 | 327758304.0056 | 343237080.6412 | 359284947.1685 | 375920683.8469 | 393163654.2672 | 411033822.781
Residential (N-1) | Value for Flex-2 | 53475109.1161 | 4633243.5483 | 4770793.6071 | 4900302.2687 | 5033329.0004 | 5170225.4428 | 5312425.0351 | 5458066.4273 | 5585896.7397 | 5716482.1477 | 5849955.4389 | 6011657.6118 | 6177632.5424 | 6348154.5444 | 6522771.8228 | 6702066.4532 | 6885889.1829 | 7074412.2592 | 7266006.7941 | 7462132.993 | 7663132.3015 | 7869037.3536 | 8077746.2768 | 8291430.2625 | 8510049.4399 | 8733980.1779 | 8960381.4919 | 9191542.5672
Commerical(N-1) | Value for Flex-2 | 241047180.1194 | 20885049.3358 | 21505077.1273 | 22088857.0988 | 22688495.306 | 23305576.8221 | 23946563.0922 | 24603063.7983 | 25179278.3558 | 25767911.9255 | 26369563.0674 | 27098460.1831 | 27846617.4034 | 28615271.2387 | 29402385.1553 | 30210582.9461 | 31039191.8333 | 31888988.2462 | 32752629.7263 | 33636698.3698 | 34542733.2959 | 35470881.606 | 36411668.7916 | 37374881.8276 | 38360340.9897 | 39369742.8188 | 40390281.1442 | 41432274.8172
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 294522289.2355 | 25518292.8842 | 26275870.7344 | 26989159.3675 | 27721824.3065 | 28475802.265 | 29258988.1274 | 30061130.2256 | 30765175.0955 | 31484394.0733 | 32219518.5064 | 33110117.795 | 34024249.9458 | 34963425.7831 | 35925156.9781 | 36912649.3993 | 37925081.0163 | 38963400.5054 | 40018636.5205 | 41098831.3627 | 42205865.5974 | 43339918.9596 | 44489415.0684 | 45666312.0901 | 46870390.4295 | 48103722.9967 | 49350662.6362 | 50623817.3844
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 175851094.6125 | 12311267.3461 | 13409297.589 | 14134718.1318 | 14916869.3938 | 15731542.5257 | 16634785.544 | 17527795.189 | 17700803.1928 | 17736497.1808 | 17813893.3966 | 18889864.9578 | 19937712.1496 | 21185354.6635 | 22374288.6742 | 23734941.6325 | 24995759.0206 | 26226140.5593 | 27630716.8564 | 29179870.5135 | 30782900.5504 | 32262754.1843 | 33802002.2581 | 35475056.3796 | 36996533.5236 | 38655870.699 | 40176813.4636 | 41572424.9694
Aggregate ($M) |  | 2205.7675 | 116860778.5499 | 135004115.3752 | 153051700.4573 | 171979361.2238 | 191718753.0535 | 210925393.6334 | 233473398.1475 | 232663027.4672 | 231724116.4995 | 209880607.5442 | 233979122.17 | 265324935.2798 | 281347546.509 | 296404718.2667 | 311540142.4258 | 330077078.2203 | 349915699.8457 | 369108771.3544 | 391979668.5973 | 414912177.1161 | 441322047.3117 | 469004459.743 | 498137726.3648 | 529400852.3623 | 561709111.7946 | 593564944.8035 | 625176467.7263
Aggregate ($M)+ Monetized Losses |  | 2208.9614 | 117090764.9499 | 135248447.8185 | 153310952.5045 | 172254126.1474 | 192009644.4647 | 211233046.1286 | 233798467.9736 | 232975073.8631 | 232065155.4558 | 210252191.3888 | 234362687.8451 | 265721131.7738 | 281756765.6344 | 296827363.5322 | 311976629.3765 | 330527834.7871 | 350381166.7051 | 369589402.2982 | 392475930.9129 | 415424551.9777 | 441851030.1827 | 469550560.7897 | 498701470.8815 | 529982781.2095 | 562309781.8484 | 594184929.4187 | 625816357.2123
Project Cost |  | 469
Benefit-Cost Ratio |  | 4.7099

## Valley S to Valley N to Vista
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Valley South to Valley North to Vista | Losses (MWh) | 49328.2 | 49736.2913 | 50144.3827 | 50552.474 | 50960.5654 | 51368.6567 | 51776.7481 | 51089 | 50877.45 | 50664.2 | 51004.825 | 51341.9516 | 51679.0781 | 52016.2047 | 52353.3312 | 52690.4578 | 53027.5844 | 53364.7109 | 53701.8375 | 54038.9641 | 54376.0906 | 54713.2172 | 55050.3437 | 55387.4703 | 55724.5969 | 56061.7234 | 56398.85
N-1 |  | EENS | 5.8 | 14.4833 | 23.1667 | 31.85 | 40.5333 | 49.2167 | 57.9 | 52.5 | 44.1 | 35.9 | 48.5 | 61.1 | 82.38 | 103.66 | 124.94 | 146.22 | 167.5 | 220.02 | 272.54 | 325.06 | 377.58 | 430.1 | 490.7 | 551.3 | 611.9 | 672.5 | 733.1
N-1 |  | IP | 3 | 4.9167 | 6.8333 | 8.75 | 10.6667 | 12.5833 | 14.5 | 13.5 | 11.8 | 10.1 | 12.9 | 15.1 | 17.26 | 19.42 | 21.58 | 23.74 | 25.9 | 27.82 | 29.74 | 31.66 | 33.58 | 35.5 | 36.58 | 37.66 | 38.74 | 39.82 | 40.9
N-1 |  | SAIDI | 0.015894 | 0.083764 | 0.15163 | 0.2195 | 0.28737 | 0.35524 | 0.42311 | 0.33569 | 0.28198 | 0.19676 | 0.31012 | 0.4465 | 0.87624 | 1.306 | 1.7357 | 2.1655 | 2.5952 | 4.3788 | 6.1623 | 7.9458 | 9.7293 | 11.5128 | 14.8115 | 18.1102 | 21.4089 | 24.7076 | 28.0063
N-1 |  | SAIFI | 0.005298 | 0.01323 | 0.021162 | 0.029094 | 0.037025 | 0.044957 | 0.052889 | 0.047956 | 0.040283 | 0.032793 | 0.044303 | 0.055812 | 0.075253 | 0.094694 | 0.11414 | 0.13358 | 0.15302 | 0.20155 | 0.25009 | 0.29862 | 0.34715 | 0.39569 | 0.45221 | 0.50874 | 0.56527 | 0.62179 | 0.67832
N-1 |  | PFD | 3 | 3.8333 | 4.6667 | 5.5 | 6.3333 | 7.1667 | 8 | 7 | 7 | 6 | 7 | 8 | 9.8 | 11.6 | 13.4 | 15.2 | 17 | 19.6 | 22.2 | 24.8 | 27.4 | 30 | 32.8 | 35.6 | 38.4 | 41.2 | 44
N-1 |  | Deficit Flex-1 | 3808.3607 | 5063.9626 | 6319.5645 | 7575.1665 | 8830.7684 | 10086.3703 | 11341.9723 | 10868.4556 | 10394.9389 | 9921.4223 | 10158.1806 | 11732.4477 | 12452.8192 | 13173.1908 | 13893.5623 | 14613.9339 | 15334.3054 | 16054.677 | 16775.0485 | 17495.4201 | 18215.7916 | 18936.1632 | 19656.5347 | 20376.9063 | 21097.2778 | 21817.6494 | 22538.0209
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 15863.8465 | 17648.2938 | 18532.2445 | 19475.1482 | 20493.6788 | 21703.1962 | 22945.9872 | 22121.1674 | 21313.2168 | 20520.3431 | 21799.1819 | 23155.1608 | 24606.2129 | 26062.5347 | 27614.3526 | 29256.497 | 30979.0521 | 32583.3718 | 34238.6898 | 35926.361 | 37681.7452 | 39178.6708 | 40662.7614 | 42131.1117 | 43588.0399 | 44646.03 | 45597.0962
N-0 |  | EENS(Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS(Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 23.4 | 45.6 | 67.8
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 13 | 24.8 | 36.6
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010438 | 0.098983 | 0.19692 | 0.29486
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010438 | 0.020353 | 0.039663 | 0.058972
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.3333 | 3.6667 | 5
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6994.7817 | 167735.6248 | 356801.1495 | 844489.8402
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41845.5858 | 1003461.6962 | 2036605.0335 | 4817272.6303
N-1 Monetized | Residential | $ | 1269.4985 | 3507.3999 | 5745.3013 | 7983.2026 | 10221.104 | 12459.0054 | 14696.9068 | 13659.3661 | 11760.7142 | 9813.2626 | 13588.9086 | 17547.2036 | 24911.6828 | 32276.162 | 39640.6412 | 47005.1204 | 54369.5996 | 77256.7859 | 100143.9722 | 123031.1586 | 145918.3449 | 168805.5312 | 204593.5776 | 240381.624 | 276169.6704 | 311957.7168 | 347745.7632
N-1 Monetized | Commercial | $ | 5267.7659 | 14553.906 | 23840.0461 | 33126.1863 | 42412.3264 | 51698.4665 | 60984.6067 | 56679.3462 | 48800.9171 | 40719.9943 | 56386.9837 | 72811.8726 | 103370.6747 | 133929.4768 | 164488.2789 | 195047.081 | 225605.8831 | 320575.9384 | 415545.9936 | 510516.0489 | 605486.1042 | 700456.1595 | 848958.1509 | 997460.1423 | 1145962.1336 | 1294464.125 | 1442966.1164
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 4851883.8074 | 5548866.4784 | 5954619.7491 | 6363793.1776 | 6862681.5292 | 7430776.4174 | 7958064.5941 | 7957168.049 | 7874171.1774 | 7776287.7266 | 8450702.8694 | 9080603.7964 | 9916810.716 | 10742147.0818 | 11532452.8263 | 12410650.1702 | 13427370.4397 | 14508754.4423 | 15576671.5917 | 16678510.3769 | 17727086.4233 | 18931202.4562 | 20126360.6731 | 21277070.9728 | 22513024.6587 | 23603677.4869 | 24710377.8006
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 7386.6021 | Losses (MWh) | 338.8 | 367.499 | 396.1981 | 424.8971 | 453.5962 | 482.2952 | 510.9942 | 609.1846 | 1110.9038 | 1614.3231 | 1563.8673 | 1516.91 | 1469.9526 | 1422.9953 | 1376.038 | 1329.0806 | 1282.1233 | 1235.166 | 1188.2087 | 1141.2513 | 1094.294 | 1047.3367 | 1000.3793 | 953.422 | 906.4647 | 859.5073 | 812.55
| 387169.6632 | Losses ($) | 13552 | 15067.4606 | 16650.2242 | 18302.7088 | 20027.4113 | 21826.9097 | 23703.8658 | 28965.1629 | 54141.1386 | 80642.7325 | 80075.2948 | 79612.6936 | 79076.9153 | 78464.5902 | 77772.2257 | 76996.2027 | 76132.7708 | 75178.0448 | 74127.9994 | 72978.4655 | 71725.1249 | 70363.5058 | 68888.9774 | 67296.7455 | 65581.8464 | 63739.1418 | 61763.3134
N-1 | 114.4291 | EENS | 4.2 | 6.0167 | 6.7133 | 7.41 | 8.1067 | 8.8033 | 9.5 | 5.1 | 5.7 | 5.6 | 5.2 | 13.9667 | 14.0533 | 14.14 | 14.2267 | 14.3133 | 14.4 | 24.21 | 34.02 | 43.83 | 53.64 | 23.6 | 33.3 | 43 | 52.7 | 62.4 | 72.1
N-1 | -30.4126 | IP | -1 | -1.9167 | -2.1533 | -2.39 | -2.6267 | -2.8633 | -3.1 | -3.3 | -3.2 | -3.3 | -3.3 | -3.7667 | -4.1933 | -4.62 | -5.0467 | -5.4733 | -5.9 | -5.96 | -6.02 | -6.08 | -6.14 | -6.2 | -6.1 | -6 | -5.9 | -5.8 | -5.7
N-1 | 54.4087 | SAIDI | 0.068918 | 0.15907 | 0.18883 | 0.21859 | 0.24835 | 0.27811 | 0.30787 | 0.28195 | 0.24759 | 0.28509 | 0.25669 | 0.52331 | 0.49656 | 0.4698 | 0.44305 | 0.4163 | 0.38955 | 16.6918 | 32.994 | 49.2962 | 65.5984 | 81.9007 | 66.2507 | 50.6007 | 34.9507 | 19.3008 | 3.6508
N-1 | 0.65104 | SAIFI | 0.00075996 | 0.0045419 | 0.0038851 | 0.0032282 | 0.0025714 | 0.0019146 | 0.0012578 | -0.0022394 | -0.0012916 | -0.0010002 | -0.00209 | 0.0039543 | 0.002067 | 0.00017976 | -0.0017075 | -0.0035948 | -0.005482 | 0.19896 | 0.4034 | 0.60784 | 0.81228 | 1.0167 | 0.81881 | 0.62089 | 0.42298 | 0.22506 | 0.027145
N-1 | 225.5303 | PFD | 11 | 17.1667 | 18.5333 | 19.9 | 21.2667 | 22.6333 | 24 | 23 | 22 | 23 | 22 | 24.6667 | 26.5333 | 28.4 | 30.2667 | 32.1333 | 34 | 37 | 40 | 43 | 46 | 49 | 49.2 | 49.4 | 49.6 | 49.8 | 50
N-1 | 39141.4455 | Flex-1 | 1637.465 | 2177.331 | 2717.1969 | 3257.0628 | 3796.9288 | 4336.7947 | 4876.6607 | 4751.6881 | 4626.7154 | 3604.0089 | 4264.9845 | 5180.7853 | 5378.55 | 5576.3147 | 5774.0795 | 5971.8442 | 6169.609 | 6367.3737 | 6565.1384 | 6762.9032 | 6960.6679 | 7158.4327 | 7356.1974 | 7553.9621 | 7751.7269 | 7949.4916 | 8147.2564
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 479183.4057 | Flex-2-2 | 41950.3173 | 44543.4531 | 45828.8607 | 47153.3528 | 48574.548 | 50215.7648 | 51874.692 | 50778.1149 | 49693.1357 | 48611.2731 | 50344.583 | 52146.7651 | 54023.4147 | 55888.5229 | 57769.072 | 59689.4741 | 61697.8438 | 63562.3581 | 65462.1684 | 67413.8488 | 69383.773 | 71058.9731 | 72692.9097 | 74263.6867 | 75805.9061 | 76906.7651 | 77904.2708
N-0 | 3651.1526 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2079.2 | 2250 | 2420.8 | 2591.6
N-0 | 597.1428 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 177.48 | 172.52 | 167.56 | 162.6
N-0 | 54.0416 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6792 | 66.2366 | 83.794 | 101.3514
N-0 | 2.8981 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3307 | 1.7832 | 2.2357 | 2.6882
N-0 | 80.9706 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 31.2 | 31.4667 | 31.7333 | 32
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 34143.207 | 85.4671 | -38.5701 | -162.6073 | -286.6445 | -410.6816 | -534.7188 | -658.756 | -1572.2209 | -1299.1265 | -1202.7397 | -1056.4557 | 1671.6039 | 993.4792 | 315.3545 | -362.7701 | -1040.8948 | -1719.0195 | 4040.5972 | 9800.2139 | 15559.8305 | 21319.4472 | 27079.0638 | 37562.4951 | 48045.9264 | 58529.3577 | 69012.789 | 79496.2203
Commerical(N-1) | EENS | 141676.7537 | 354.6443 | -160.0462 | -674.7367 | -1189.4272 | -1704.1177 | -2218.8082 | -2733.4987 | -6523.9084 | -5390.7071 | -4990.7514 | -4383.7478 | 6936.2967 | 4122.428 | 1308.5592 | -1505.3095 | -4319.1782 | -7133.0469 | 16766.4008 | 40665.8485 | 64565.2962 | 88464.7439 | 112364.1916 | 155865.0412 | 199365.8907 | 242866.7403 | 286367.5899 | 329868.4394
Aggregate | EENS | 175819.9607 | 440.1114 | -198.6163 | -837.344 | -1476.0717 | -2114.7993 | -2753.527 | -3392.2547 | -8096.1293 | -6689.8336 | -6193.4911 | -5440.2035 | 8607.9006 | 5115.9072 | 1623.9138 | -1868.0796 | -5360.073 | -8852.0664 | 20806.998 | 50466.0623 | 80125.1267 | 109784.1911 | 139443.2555 | 193427.5363 | 247411.8171 | 301396.098 | 355380.3788 | 409364.6597
Residential (N-0) | EENS | 24212192.0993 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15543246.7169 | 17584078.6321 | 19396291.004 | 20829038.5593
Commerical(N-0) | EENS | 110981417.4476 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69171640.5729 | 78550030.3969 | 87122315.029 | 93547197.1047
Aggregate | EENS | 135193609.5469 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84714887.2898 | 96134109.029 | 106518606.033 | 114376235.664
Residential (N-1) | Value for Flex-1 | 207361752.6799 | 6621897.889 | 9025240.0833 | 11544610.7011 | 14184309.0748 | 16948776.9855 | 19842603.0985 | 22870527.5316 | 22841542.6096 | 22796814.3618 | 18201663.851 | 22078347.207 | 27489608.933 | 29252436.5342 | 31086224.5099 | 32993419.1115 | 34976544.5529 | 37038205.3794 | 39181088.9069 | 41407967.7324 | 43721702.3186 | 46125243.6543 | 48621635.9928 | 51214019.671 | 53905634.0105 | 56699820.3048 | 59600024.8925 | 62609802.3219
Commerical(N-1) | Value for Flex-1 | 854254218.5995 | 27279785.8511 | 37180672.4982 | 47559553.6114 | 58434140.8601 | 69822732.7501 | 81744232.8966 | 94218168.8424 | 94098761.6153 | 93914497.6713 | 74984166.2182 | 90954677.0199 | 113247086.7709 | 120509288.6742 | 128063821.2434 | 135920762.1357 | 144090510.1843 | 152583795.159 | 161411687.8136 | 170585610.2289 | 180117346.4601 | 190019053.4965 | 200303272.5432 | 210982940.6337 | 222071402.5835 | 233582423.2928 | 245530200.411 | 257929377.3705
Aggregate | Value for Flex-1 | 1061615971.2793 | 33901683.7401 | 46205912.5815 | 59104164.3126 | 72618449.9349 | 86771509.7356 | 101586835.9951 | 117088696.374 | 116940304.2249 | 116711312.0331 | 93185830.0692 | 113033024.2269 | 140736695.704 | 149761725.2085 | 159150045.7534 | 168914181.2472 | 179067054.7372 | 189622000.5384 | 200592776.7205 | 211993577.9613 | 223839048.7787 | 236144297.1508 | 248924908.536 | 262196960.3047 | 275977036.594 | 290282243.5976 | 305130225.3035 | 320539179.6924
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1 and 2) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 158850774.4516 | 11220634.2188 | 12144918.1584 | 12786910.2509 | 13549003.8391 | 14198581.0583 | 15000915.7058 | 15909014.2717 | 15943271.5953 | 15999716.4072 | 16077364.9697 | 17017237.4897 | 18089024.9798 | 19073573.1791 | 20183246.8534 | 21490829.7021 | 22579839.7873 | 23724942.3552 | 24911056.9306 | 26196805.9595 | 27625844.3348 | 29110039.0485 | 30411440.883 | 31944711.5843 | 33332991.3303 | 34748837.6652 | 36032493.5279 | 37232773.5323
Aggregate ($M) |  | 1355.8362 | 46186416.015 | 61030693.7386 | 75823553.0558 | 91447167.7399 | 107619710.7541 | 123194795.4827 | 142105261.8508 | 140635817.5108 | 139232771.3537 | 116937348.717 | 137617805.6599 | 169574939.7199 | 182678413.1563 | 194931145.2106 | 207214698.4501 | 222706912.1605 | 239510927.0138 | 255387446.2078 | 274818552.1596 | 294319041.9801 | 317391902.5198 | 341421826.1392 | 366847397.4144 | 394272327.0312 | 421466586.3898 | 448036705.2432 | 472557553.5485
Aggregate ($M)+ Monetized Losses |  | 1356.2233 | 46199968.015 | 61045761.1992 | 75840203.28 | 91465470.4487 | 107639738.1653 | 123216622.3923 | 142128965.7166 | 140664782.6737 | 139286912.4923 | 117017991.4495 | 137697880.9547 | 169654552.4135 | 182757490.0717 | 195009609.8008 | 207292470.6758 | 222783908.3632 | 239587059.7847 | 255462624.2526 | 274892680.159 | 294392020.4456 | 317463627.6447 | 341492189.645 | 366916286.3919 | 394339623.7768 | 421532168.2362 | 448100444.385 | 472619316.8618
Project Cost |  | 270
Benefit-Cost Ratio |  | 5.023

## Centralized BESS in Valley S
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Centralized BESS in Valley South | Losses (MWh) | 48531.45 | 48910.8731 | 49290.2962 | 49669.7192 | 50049.1423 | 50428.5654 | 50807.9885 | 50219.15 | 50017.85 | 49814 | 50139.1 | 50455.3594 | 50771.6187 | 51087.8781 | 51404.1375 | 51720.3969 | 52036.6562 | 52352.9156 | 52669.175 | 52985.4344 | 53301.6938 | 53617.9531 | 53934.2125 | 54250.4719 | 54566.7313 | 54882.9906 | 55199.25
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | Deficit Flex-1 | 1868.1179 | 2484.0292 | 3099.9405 | 3715.8518 | 4331.7632 | 4947.6745 | 5563.5858 | 5501.2179 | 5438.85 | 5376.4821 | 5407.6661 | 6876.5094 | 7331.8177 | 7787.126 | 8242.4343 | 8697.7427 | 9153.051 | 9608.3593 | 10063.6676 | 10518.9759 | 10974.2843 | 11429.5926 | 11884.9009 | 12340.2092 | 12795.5175 | 13250.8258 | 13706.1342
N-1 |  | Deficit Flex-2-1 | 192864.6017 | 195239.3177 | 196366.7753 | 197525.4186 | 198743.8771 | 200140.9293 | 201537.6406 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57792.8146 | 62126.796 | 64269.8063 | 66510.3186 | 68915.1853 | 71720.6292 | 74566.1719 | 72681.8696 | 70823.43 | 68977.7626 | 71941.0617 | 75038.395 | 78295.631 | 81542.3252 | 84891.8975 | 88351.148 | 91958.3516 | 95296.185 | 98685.3392 | 102124.6006 | 105622.5671 | 108598.2389 | 111520.8846 | 114357.8523 | 117139.0932 | 119135.7737 | 120939.4269
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 16067229.4426 | 17677237.6168 | 18717757.5949 | 19881255.1753 | 21019506.8395 | 22376241.6863 | 23794189.7734 | 23836575.0017 | 23818798.2536 | 23806131.1223 | 25403815.3468 | 27084189.8883 | 28879382.0559 | 30786183.8526 | 32851759.1792 | 34781652.2015 | 36893354.5337 | 39105422.0446 | 41389020.5285 | 43831671.0472 | 46265962.2967 | 48676490.0023 | 51305915.2589 | 53755982.9155 | 56293011.2814 | 58570619.4241 | 60789046.308
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component |  |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 15781.6969 | Losses (MWh) | 1135.55 | 1192.9173 | 1250.2846 | 1307.6519 | 1365.0192 | 1422.3865 | 1479.7538 | 1479.0346 | 1970.5038 | 2464.5231 | 2429.5923 | 2403.5022 | 2377.412 | 2351.3219 | 2325.2317 | 2299.1416 | 2273.0514 | 2246.9613 | 2220.8712 | 2194.781 | 2168.6909 | 2142.6007 | 2116.5106 | 2090.4204 | 2064.3303 | 2038.2401 | 2012.15
| 806178.5419 | Losses ($) | 45422 | 48909.6096 | 52543.211 | 56327.9239 | 60269.0329 | 64371.9925 | 68642.4318 | 70324.2951 | 96034.7038 | 123114.0644 | 124403.3425 | 126144.1248 | 127894.1942 | 129652.927 | 131419.6625 | 133193.7018 | 134974.3057 | 136760.6937 | 138552.0422 | 140347.4827 | 142146.1002 | 143946.9314 | 145748.9629 | 147551.1291 | 149352.3104 | 151151.3315 | 152946.9583
N-1 | 1008.9296 | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 | 100.1707 | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 | 73.3366 | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 | 1.4722 | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 | 315.9581 | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-1 | 82124.1153 | Flex-1 | 3577.7078 | 4757.2643 | 5936.8209 | 7116.3775 | 8295.934 | 9475.4906 | 10655.0472 | 10118.9258 | 9582.8044 | 8148.949 | 9015.499 | 10036.7236 | 10499.5515 | 10962.3795 | 11425.2075 | 11888.0354 | 12350.8634 | 12813.6914 | 13276.5194 | 13739.3473 | 14202.1753 | 14665.0033 | 15127.8312 | 15590.6592 | 16053.4872 | 16516.3151 | 16979.1431
N-1 | 0.029234 | Flex-2-1 | 0.064497 | -0.075755 | -0.0098416 | -0.043008 | 0.046789 | 0.0091605 | 0.069676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 3460.9343 | Flex-2-2 | 21.3492 | 64.9509 | 91.299 | 118.1824 | 153.0414 | 198.3318 | 254.5073 | 217.4126 | 182.9226 | 153.8535 | 202.7032 | 263.5309 | 333.9965 | 408.7323 | 491.5272 | 594.8232 | 718.5443 | 849.5449 | 1015.5189 | 1215.6092 | 1442.9511 | 1639.4051 | 1834.7864 | 2036.9462 | 2254.8528 | 2417.0214 | 2561.9401
N-0 | 3662.4319 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 | 603.3371 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 | 54.0898 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 | 2.9079 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 | 81.9765 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 355030.5479 | 1354.9655 | 3468.8297 | 5582.694 | 7696.5582 | 9810.4224 | 11924.2866 | 14038.1508 | 12087.1452 | 10461.5877 | 8610.5229 | 12532.4529 | 19218.8075 | 25905.162 | 32591.5165 | 39277.8711 | 45964.2256 | 52650.5801 | 81297.3831 | 109944.1861 | 138590.9891 | 167237.792 | 195884.595 | 242156.0727 | 288427.5504 | 334699.0281 | 380970.5058 | 427241.9834
Commerical(N-1) | EENS | 1473194.2274 | 5622.4102 | 14393.8598 | 23165.3095 | 31936.7591 | 40708.2087 | 49479.6583 | 58251.108 | 50155.4378 | 43410.21 | 35729.2429 | 52003.2359 | 79748.1693 | 107493.1026 | 135238.036 | 162982.9694 | 190727.9028 | 218472.8361 | 337342.3391 | 456211.8421 | 575081.3451 | 693950.8481 | 812820.3511 | 1004823.1921 | 1196826.033 | 1388828.8739 | 1580831.7149 | 1772834.5558
Aggregate | EENS | 1828224.7753 | 6977.3757 | 17862.6896 | 28748.0034 | 39633.3173 | 50518.6311 | 61403.9449 | 72289.2588 | 62242.583 | 53871.7977 | 44339.7658 | 64535.6888 | 98966.9767 | 133398.2646 | 167829.5525 | 202260.8405 | 236692.1284 | 271123.4163 | 418639.7222 | 566156.0282 | 713672.3342 | 861188.6402 | 1008704.9462 | 1246979.2648 | 1485253.5834 | 1723527.902 | 1961802.2206 | 2200076.5392
Residential (N-0) | EENS | 24322736.8672 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21673528.3995
Commerical(N-0) | EENS | 111616614.0139 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98364469.7349
Aggregate | EENS | 135939350.8811 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 120037998.1344
Residential (N-1) | Value for Flex-1 | 432939381.8364 | 14468227.0973 | 19719304.8461 | 25223893.8403 | 30991387.7188 | 37031491.3575 | 43354230.5609 | 49969962.0423 | 48642055.4264 | 47216522.2535 | 41155401.2508 | 46670115.4262 | 53255557.2129 | 57104138.6596 | 61111864.4553 | 65284286.4542 | 69627134.6377 | 74146322.5514 | 78847952.9016 | 83738323.3177 | 88823932.2841 | 94111485.2467 | 99607900.8997 | 105320317.6572 | 111256100.3144 | 117422846.906 | 123828395.7644 | 130480832.7865
Commerical(N-1) | Value for Flex-1 | 1783551154.2119 | 59603778.7768 | 81236289.4067 | 103913173.2064 | 127673128.5152 | 152556135.8561 | 178603497.8588 | 205857880.3767 | 200387393.1058 | 194514720.2961 | 169545129.1393 | 192263724.9645 | 219393325.071 | 235248066.3333 | 251758423.8306 | 268947269.1612 | 286838207.7435 | 305455601.2117 | 324824590.4735 | 344971119.4476 | 365921959.5014 | 387704734.6082 | 410347947.2456 | 433881005.0558 | 458334248.2895 | 483738978.0567 | 510127485.4071 | 537533081.2637
Aggregate | Value for Flex-1 | 2216490536.0483 | 74072005.8741 | 100955594.2528 | 129137067.0467 | 158664516.234 | 189587627.2136 | 221957728.4197 | 255827842.419 | 249029448.5322 | 241731242.5495 | 210700530.3901 | 238933840.3907 | 272648882.2839 | 292352204.9929 | 312870288.2859 | 334231555.6154 | 356465342.3812 | 379601923.7631 | 403672543.3751 | 428709442.7653 | 454745891.7855 | 481816219.8549 | 509955848.1454 | 539201322.713 | 569590348.6039 | 601161824.9627 | 633955881.1715 | 668013914.0502
Residential (N-1) | Value for Flex-2 | 8.245 | 2.2011 | 2.65 | 0.35288 | 1.5806 | 1.7626 | 0.35371 | 2.7576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 334.4915 | 89.2977 | 107.5082 | 14.3159 | 64.1242 | 71.5056 | 14.3497 | 111.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 342.7365 | 91.4988 | 110.1583 | 14.6688 | 65.7048 | 73.2681 | 14.7035 | 114.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 1267956.9556 | 5288.5836 | 16547.0199 | 23772.4051 | 31541.8413 | 41755.7479 | 55450.4369 | 72889.0924 | 63864.6427 | 55089.331 | 47521.574 | 64125.0123 | 85438.8879 | 111001.8392 | 139210.0826 | 171523.3492 | 208837.756 | 258958.2612 | 314389.3282 | 384457.0226 | 472683.6645 | 571163.1751 | 666153.3369 | 765156.9985 | 854079.3876 | 968851.0426 | 1065551.5908 | 1154105.0249
Aggregate ($M) |  | 2355.5264 | 75148021.2769 | 103670175.7356 | 133122917.9603 | 164016947.1349 | 196331709.6203 | 228684394.8138 | 265084078.8617 | 256915893.5778 | 248368636.4253 | 218472738.899 | 246635485.2386 | 283573899.284 | 306434603.9583 | 328773556.6111 | 351416895.3853 | 377976249.9745 | 406304841.6271 | 434268377.9843 | 466237757.9926 | 498706271.524 | 535276353.7995 | 573576739.8933 | 613725756.9654 | 656693409.2321 | 701159510.2572 | 745895247.1988 | 791406093.7488
Aggregate ($M)+ Monetized Losses |  | 2356.3326 | 75193443.2769 | 103719085.3452 | 133175461.1712 | 164073275.0588 | 196391978.6532 | 228748766.8063 | 265152721.2936 | 256986217.8728 | 248464671.1291 | 218595852.9634 | 246759888.5811 | 283700043.4088 | 306562498.1525 | 328903209.538 | 351548315.0479 | 378109443.6763 | 406439815.9328 | 434405138.6781 | 466376310.0349 | 498846619.0068 | 535418499.8997 | 573720686.8247 | 613871505.9283 | 656840960.3612 | 701308862.5677 | 746046398.5303 | 791559040.7071
Project Cost |  | 417
Benefit-Cost Ratio |  | 5.6507
Market Participation Revenue (All costs are $x1,000) |  |  | 2973.7374 | 3059.1177 | 3144.498 | 3229.8782 | 3315.2585 | 3400.6387 | 4101.6106 | 4802.5824 | 5503.5543 | 6204.5261 | 6905.498 | 7680.937 | 8456.3759 | 9231.8149 | 10007.2539 | 10782.6929 | 11558.63 | 12334.5671 | 13110.5043 | 13886.4414 | 14662.3785 | 14830.0258 | 14997.6731 | 15165.3204 | 15332.9677 | 15500.6149 | 15668.2622

## MiraLoma & Centralized BESS VS
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Mira Loma and Centralized BESS in Valley South | Losses (MWh) | 48453.3 | 48868.5423 | 49283.7846 | 49699.0269 | 50114.2692 | 50529.5115 | 50805.9144 | 50242.6 | 50024.2 | 49809.375 | 50155 | 50497.7984 | 50840.5969 | 51183.3953 | 51510.8091 | 51838.223 | 52165.6368 | 52493.0506 | 52820.4644 | 53147.8782 | 53475.2921 | 53802.7059 | 54130.1197 | 54457.5335 | 54784.9474 | 55112.3612 | 55439.775
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 29.4 | 22.7 | 17.3 | 15 | 20.5 | 26.6 | 44.4667 | 56.45 | 53.84 | 62.92 | 72 | 78.88 | 85.76 | 92.64 | 99.52 | 106.4 | 117.26 | 128.12 | 138.98 | 149.84 | 160.7
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.8 | 7.2 | 5.5 | 8.3 | 10.5 | 12.2333 | 14.2 | 13.26 | 14.18 | 15.1 | 14.86 | 14.62 | 14.38 | 14.14 | 13.9 | 15.44 | 16.98 | 18.52 | 20.06 | 21.6
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0.15146 | 0.093554 | 0.071299 | 0.06182 | 0.084487 | 0.13703 | 0.36345 | 0.50293 | 0.49992 | 0.62088 | 0.74184 | 1.1197 | 1.4975 | 1.8754 | 2.2532 | 2.6311 | 3.1645 | 3.698 | 4.2314 | 4.7649 | 5.2984
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0.030292 | 0.023388 | 0.017825 | 0.015455 | 0.021122 | 0.027407 | 0.04579 | 0.058125 | 0.055473 | 0.064828 | 0.074184 | 0.081272 | 0.088361 | 0.09545 | 0.10254 | 0.10963 | 0.12082 | 0.13201 | 0.1432 | 0.15438 | 0.16557
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 4 | 4 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 12.8 | 15.6 | 18.4 | 21.2 | 24 | 25.6 | 27.2 | 28.8 | 30.4 | 32
N-1 |  | Deficit Flex-1 | 2180.0835 | 2898.8487 | 3617.6139 | 4336.3791 | 5055.1443 | 5773.9095 | 6492.6746 | 6092.5267 | 5692.3787 | 5292.2308 | 5708 | 5964.2406 | 6199.164 | 6534.0874 | 6672.7659 | 6811.4444 | 6950.1229 | 7088.8014 | 7227.4799 | 7366.1584 | 7504.8368 | 7643.5153 | 7782.1938 | 7920.8723 | 8059.5508 | 8198.2293 | 8336.9078
N-1 |  | Deficit Flex-2-1 | 139482.7176 | 141661.1434 | 142695.4071 | 143758.2787 | 144876.0214 | 146157.5954 | 147438.8568 | 146594.2185 | 145749.5803 | 144904.7857 | 146257.9578 | 147648.4922 | 149079.3591 | 150483.8067 | 151918.7381 | 153379.6199 | 154874.5812 | 156234.0064 | 157599.5284 | 158964.5814 | 160338.3887 | 161484.7393 | 162604.0453 | 163685.9889 | 164738.2303 | 165489.2283 | 166160.3429
N-1 |  | Deficit Flex-2-2 | 18207.4584 | 20177.9506 | 21154.9937 | 22187.8326 | 23306.0057 | 24628.6125 | 25977.651 | 25085.8101 | 24204.4899 | 23335.3402 | 24733.5106 | 26201.7967 | 27781.6878 | 29389.983 | 31072.602 | 32829.5502 | 34677.1444 | 36397.4901 | 38187.068 | 40009.7945 | 41888.713 | 43498.5243 | 45101.3841 | 46679.9631 | 48252.2118 | 49385.5978 | 50403.8917
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 7462.6781 | 5906.0497 | 4613.6135 | 4100.249 | 5743.7655 | 10222.7156 | 14701.6657 | 19180.6158 | 17092.5371 | 20243.6468 | 23394.7564 | 26538.8709 | 29682.9854 | 32827.0999 | 35971.2144 | 39115.3289 | 44660.39 | 50205.451 | 55750.5121 | 61295.5732 | 66840.6342
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 30966.277 | 33256.8243 | 35547.3716 | 37837.9189 | 23833.6735 | 42419.0135 | 61004.3534 | 79589.6934 | 51076.49 | 54227.5997 | 97076.2102 | 110122.6688 | 123169.1273 | 136215.5859 | 149262.0444 | 162308.503 | 185317.6553 | 208326.8076 | 231335.9599 | 254345.1122 | 277354.2645
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5590035.4665 | 6282480.6097 | 6730600.6141 | 7226584.158 | 7694667.9842 | 8351447.6567 | 9003229.9816 | 8936987.4783 | 8835154.9115 | 8718533.6489 | 9475291.797 | 10279986.071 | 11008354.5464 | 11873656.1194 | 12823609.0576 | 13920427.5528 | 14970916.7674 | 15974526.1049 | 17110540.9974 | 18367408.4345 | 19668025.4546 | 20858191.3676 | 22155954.9722 | 23377469.9551 | 24675632.6746 | 25884999.8838 | 27123865.2689
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 15402.595 | Losses (MWh) | 1213.7 | 1235.2481 | 1256.7962 | 1278.3442 | 1299.8923 | 1321.4404 | 1481.8279 | 1455.5846 | 1964.1538 | 2469.1481 | 2413.6923 | 2361.0631 | 2308.4339 | 2255.8047 | 2218.5601 | 2181.3155 | 2144.0709 | 2106.8263 | 2069.5817 | 2032.3371 | 1995.0925 | 1957.848 | 1920.6034 | 1883.3588 | 1846.1142 | 1808.8696 | 1771.625
| 782066.8229 | Losses ($) | 48548 | 50645.1712 | 52816.8584 | 55065.4767 | 57393.5154 | 59803.5402 | 68738.6418 | 69209.3078 | 95725.2295 | 123345.104 | 123589.2087 | 123916.7757 | 124183.4778 | 124386.0671 | 125390.6934 | 126367.8098 | 127315.4129 | 128231.4162 | 129113.6475 | 129959.8458 | 130767.658 | 131534.6358 | 132258.2328 | 132935.8005 | 133564.5851 | 134141.7241 | 134664.2422
N-1 | 753.6406 | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 38 | 34.9 | 32.5 | 26.5 | 33.2 | 48.4667 | 51.9667 | 61.35 | 85.3267 | 97.6133 | 109.9 | 165.35 | 220.8 | 276.25 | 331.7 | 347.3 | 406.74 | 466.18 | 525.62 | 585.06 | 644.5
N-1 | 43.6672 | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 0.83333 | 0.83333 | 0.6 | 3.2733 | 4.0867 | 4.9 | 7 | 9.1 | 11.2 | 13.3 | 15.4 | 15.04 | 14.68 | 14.32 | 13.96 | 13.6
N-1 | 69.1726 | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.57952 | 0.52409 | 0.45828 | 0.42003 | 0.48232 | 0.83277 | 1.0093 | 1.2729 | 1.6789 | 1.9609 | 2.2429 | 19.9508 | 37.6587 | 55.3666 | 73.0745 | 90.7824 | 77.8977 | 65.013 | 52.1282 | 39.2435 | 26.3587
N-1 | 1.2092 | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.023855 | 0.022329 | 0.021167 | 0.016338 | 0.021091 | 0.03236 | 0.03153 | 0.036749 | 0.056955 | 0.065153 | 0.073352 | 0.31924 | 0.56513 | 0.81101 | 1.0569 | 1.3028 | 1.1502 | 0.99763 | 0.84505 | 0.69247 | 0.53989
N-1 | 269.1878 | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 27 | 26 | 25 | 25 | 25 | 27.6667 | 30.3333 | 33 | 35.6667 | 38.3333 | 41 | 43.8 | 46.6 | 49.4 | 52.2 | 55 | 56.4 | 57.8 | 59.2 | 60.6 | 62
N-1 | 85504.239 | Flex-1 | 3265.7422 | 4342.4449 | 5419.1475 | 6495.8502 | 7572.5529 | 8649.2556 | 9725.9583 | 9527.617 | 9329.2756 | 8233.2004 | 8715.1651 | 10948.9923 | 11632.2052 | 12215.4181 | 12994.8759 | 13774.3337 | 14553.7915 | 15333.2493 | 16112.7071 | 16892.1649 | 17671.6227 | 18451.0805 | 19230.5383 | 20009.9961 | 20789.4539 | 21568.9117 | 22348.3695
N-1 | 499595.179 | Flex-2-1 | 53381.9486 | 53578.0986 | 53671.3584 | 53767.0968 | 53867.9025 | 53983.343 | 54098.8535 | 54022.6764 | 53946.569 | 53870.4476 | 53992.3771 | 54117.6733 | 54246.6037 | 54373.1535 | 54502.4502 | 54634.0851 | 54768.7908 | 54891.2838 | 55014.3262 | 55137.3263 | 55261.1153 | 55364.4089 | 55465.2656 | 55562.7558 | 55657.5695 | 55725.2393 | 55785.7111
N-1 | 451168.6674 | Flex-2-2 | 39606.7054 | 42013.7963 | 43206.1115 | 44440.6684 | 45762.221 | 47290.3485 | 48843.0282 | 47813.4722 | 46801.8627 | 45796.276 | 47410.2544 | 49100.1292 | 50847.9397 | 52561.0746 | 54310.8226 | 56116.4209 | 57999.7515 | 59748.2398 | 61513.7902 | 63330.4153 | 65176.8052 | 66739.1196 | 68254.2869 | 69714.8354 | 71141.7342 | 72167.1972 | 73097.4753
N-0 | 3662.4319 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 | 603.3371 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 | 54.0898 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 | 2.9079 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 | 81.9765 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 267558.6437 | 1354.9655 | 3468.8297 | 5582.694 | 7696.5582 | 9810.4224 | 11924.2866 | 6575.4728 | 6181.0955 | 5847.9742 | 4510.2739 | 6788.6875 | 8996.0919 | 11203.4963 | 13410.9008 | 22185.334 | 25720.5788 | 29255.8237 | 54758.5122 | 80261.2007 | 105763.8892 | 131266.5776 | 156769.2661 | 197495.6827 | 238222.0994 | 278948.516 | 319674.9326 | 360401.3492
Commerical(N-1) | EENS | 1102394.9786 | 5622.4102 | 14393.8598 | 23165.3095 | 31936.7591 | 40708.2087 | 49479.6583 | 27284.831 | 16898.6135 | 7862.8385 | -2108.676 | 28169.5624 | 37329.1558 | 46488.7492 | 55648.3426 | 111906.4794 | 136500.3031 | 121396.6259 | 227219.6703 | 333042.7148 | 438865.7593 | 544688.8037 | 650511.8482 | 819505.5368 | 988499.2254 | 1157492.914 | 1326486.6026 | 1495480.2913
Aggregate | EENS | 1369953.6223 | 6977.3757 | 17862.6896 | 28748.0034 | 39633.3173 | 50518.6311 | 61403.9449 | 33860.3038 | 23079.709 | 13710.8127 | 2401.5979 | 34958.2498 | 46325.2477 | 57692.2455 | 69059.2434 | 134091.8134 | 162220.8819 | 150652.4496 | 281978.1825 | 413303.9155 | 544629.6484 | 675955.3814 | 807281.1143 | 1017001.2195 | 1226721.3248 | 1436441.43 | 1646161.5352 | 1855881.6405
Residential (N-0) | EENS | 24322736.8672 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21673528.3995
Commerical(N-0) | EENS | 111616614.0139 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98364469.7349
Aggregate | EENS | 135939350.8811 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 120037998.1344
Residential (N-1) | Value for Flex-1 | 461519492.4693 | 13206640.1538 | 17999839.333 | 23024444.3211 | 28289029.659 | 33802453.9861 | 39573868.886 | 45612727.9971 | 45799611.9601 | 45967332.1661 | 41580903.7386 | 45115390.6724 | 58096118.9648 | 63264326.8193 | 68097166.019 | 74253461.4246 | 80675010.8717 | 87371229.3777 | 94351836.9273 | 101626867.836 | 109206680.392 | 117101966.7835 | 125323763.3193 | 133883460.9526 | 142792816.1155 | 152063961.8735 | 161709419.4093 | 171742109.8457
Commerical(N-1) | Value for Flex-1 | 1901290707.2428 | 54406504.1844 | 74152723.3715 | 94852249.4528 | 116540406.3861 | 139253688.5102 | 163029796.9864 | 187907677.3312 | 188677570.5812 | 189368516.1955 | 171298043.0229 | 185858830.3174 | 239334660.6524 | 260625777.7714 | 280535299.2757 | 305896973.9973 | 332351397.8929 | 359937357.3746 | 388694895.2066 | 418665349.0819 | 449891391.3415 | 482417069.8708 | 516287850.2071 | 551550658.8914 | 588253928.1037 | 626447641.6147 | 666183382.0962 | 707514379.8258
Aggregate | Value for Flex-1 | 2362810199.7121 | 67613144.3382 | 92152562.7045 | 117876693.7739 | 144829436.0451 | 173056142.4962 | 202603665.8724 | 233520405.3283 | 234477182.5413 | 235335848.3616 | 212878946.7615 | 230974220.9898 | 297430779.6171 | 323890104.5907 | 348632465.2947 | 380150435.4218 | 413026408.7646 | 447308586.7523 | 483046732.1339 | 520292216.9179 | 559098071.7335 | 599519036.6543 | 641611613.5263 | 685434119.844 | 731046744.2192 | 778511603.4882 | 827892801.5055 | 879256489.6715
Residential (N-1) | Value for Flex-2 | 20993140.6704 | 1821819.6755 | 1874226.7329 | 1924426.2997 | 1976055.55 | 2029254.3823 | 2084443.2126 | 2141125.9697 | 2191563.8077 | 2243188.231 | 2296023.5477 | 2358750.8421 | 2423330.2384 | 2489831.1903 | 2558030.613 | 2628216.3184 | 2700428.1162 | 2774763.4442 | 2850493.569 | 2928305.2142 | 3008223.5776 | 3090351.7816 | 3173531.4479 | 3258795.4504 | 3346136.4511 | 3435642.5475 | 3525815.175 | 3617882.3431
Commerical(N-1) | Value for Flex-2 | 94629771.5721 | 8212129.0209 | 8448361.7955 | 8674643.9708 | 8907370.6618 | 9147172.4825 | 9395944.5212 | 9651450.6622 | 9878806.8808 | 10111511.8135 | 10349675.0323 | 10632427.8432 | 10923529.2854 | 11223292.431 | 11530711.6922 | 11847084.4241 | 12172590.0756 | 12507667.8621 | 12849032.9071 | 13199780.7218 | 13560024.8889 | 13930230.2481 | 14305175.2334 | 14689515.6809 | 15083218.5136 | 15486680.8437 | 15893147.6646 | 16308154.4145
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 115622912.2425 | 10033948.6964 | 10322588.5284 | 10599070.2705 | 10883426.2117 | 11176426.8648 | 11480387.7338 | 11792576.6319 | 12070370.6885 | 12354700.0445 | 12645698.5801 | 12991178.6852 | 13346859.5239 | 13713123.6212 | 14088742.3052 | 14475300.7425 | 14873018.1918 | 15282431.3062 | 15699526.4761 | 16128085.9359 | 16568248.4665 | 17020582.0297 | 17478706.6813 | 17948311.1313 | 18429354.9647 | 18922323.3912 | 19418962.8397 | 19926036.7575
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 149022625.4435 | 10482482.5597 | 11411304.0271 | 12010929.3859 | 12686212.8587 | 13366594.6033 | 14080244.4665 | 14863848.8842 | 14963452.166 | 15038732.6731 | 15135119.0474 | 15992648.5621 | 16889642.7052 | 17982029.3488 | 19051737.8158 | 20199673.4708 | 21070062.4047 | 22181396.0274 | 23445285.2679 | 24662936.5537 | 25936946.2772 | 27169100.0172 | 28484451.9716 | 29915117.2852 | 31232592.348 | 32586229.6493 | 33751171.1311 | 34819286.064
Aggregate ($M) |  | 2764.765 | 89200210.9146 | 116584379.5646 | 144448757.27 | 173719898.4703 | 204301417.3549 | 234835499.3264 | 269321634.6078 | 269294422.9247 | 269271424.6389 | 248342513.156 | 267565990.6336 | 338454218.2294 | 369480948.6678 | 397438233.3491 | 431771057.0288 | 470197087.9519 | 511095902.7221 | 552336327.6193 | 598074245.4994 | 644921919.8654 | 696412456.2119 | 750328086.7583 | 806826847.4693 | 866699140.5139 | 928761904.3087 | 991621109.2274 | 1055895692.268
Aggregate ($M)+ Monetized Losses |  | 2765.5471 | 89248758.9146 | 116635024.7357 | 144501574.1283 | 173774963.947 | 204358810.8703 | 234895302.8666 | 269390373.2496 | 269363632.2326 | 269367149.8684 | 248465858.2601 | 267689579.8423 | 338578135.0051 | 369605132.1457 | 397562619.4162 | 431896447.7222 | 470323455.7618 | 511223218.135 | 552464559.0355 | 598203359.147 | 645051879.7112 | 696543223.8699 | 750459621.3942 | 806959105.7021 | 866832076.3144 | 928895468.8938 | 991755250.9515 | 1056030356.5102
Project Cost |  | 429
Benefit-Cost Ratio |  | 6.4465
Market Participation Revenue (All costs are $x1,000) |  |  | 2036: 3265.0389; 2037: 3851.5585; 2038: 4438.0781; 2039: 5024.5977; 2040: 5611.1173; 2041: 6197.6369; 2042: 6423.3458; 2043: 6649.0546; 2044: 6874.7634; 2045: 7100.4723; 2046: 7326.1811; 2047: 7407.5891; 2048: 7488.9971

## VS to VN & Distributed BESS VS
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Valley South to Valley North and Distributed BESS in Valley South | Losses (MWh) | 49328.2 | 49736.2913 | 50144.3827 | 50552.474 | 50960.5654 | 51368.6567 | 51776.7481 | 51089 | 50877.45 | 50664.2 | 51004.825 | 51341.9516 | 51679.0781 | 52016.2047 | 52353.3312 | 52690.4578 | 53027.5844 | 53364.7109 | 53701.8375 | 54038.9641 | 54376.0906 | 54713.2172 | 55050.3437 | 55387.4703 | 55724.5969 | 56061.7234 | 56398.85
N-1 |  | EENS | 5.8 | 14.4833 | 23.1667 | 31.85 | 40.5333 | 49.2167 | 57.9 | 52.5 | 44.1 | 35.9 | 48.5 | 61.1 | 82.38 | 103.66 | 124.94 | 146.22 | 167.5 | 220.02 | 272.54 | 325.06 | 377.58 | 430.1 | 490.7 | 551.3 | 611.9 | 672.5 | 733.1
N-1 |  | IP | 3 | 4.9167 | 6.8333 | 8.75 | 10.6667 | 12.5833 | 14.5 | 13.5 | 11.8 | 10.1 | 12.9 | 15.1 | 17.26 | 19.42 | 21.58 | 23.74 | 25.9 | 27.82 | 29.74 | 31.66 | 33.58 | 35.5 | 36.58 | 37.66 | 38.74 | 39.82 | 40.9
N-1 |  | SAIDI | 0.015894 | 0.083764 | 0.15163 | 0.2195 | 0.28737 | 0.35524 | 0.42311 | 0.33569 | 0.28198 | 0.19676 | 0.31012 | 0.4465 | 0.87624 | 1.306 | 1.7357 | 2.1655 | 2.5952 | 4.3788 | 6.1623 | 7.9458 | 9.7293 | 11.5128 | 14.8115 | 18.1102 | 21.4089 | 24.7076 | 28.0063
N-1 |  | SAIFI | 0.005298 | 0.01323 | 0.021162 | 0.029094 | 0.037025 | 0.044957 | 0.052889 | 0.047956 | 0.040283 | 0.032793 | 0.044303 | 0.055812 | 0.075253 | 0.094694 | 0.11414 | 0.13358 | 0.15302 | 0.20155 | 0.25009 | 0.29862 | 0.34715 | 0.39569 | 0.45221 | 0.50874 | 0.56527 | 0.62179 | 0.67832
N-1 |  | PFD | 3 | 3.8333 | 4.6667 | 5.5 | 6.3333 | 7.1667 | 8 | 7 | 7 | 6 | 7 | 8 | 9.8 | 11.6 | 13.4 | 15.2 | 17 | 19.6 | 22.2 | 24.8 | 27.4 | 30 | 32.8 | 35.6 | 38.4 | 41.2 | 44
N-1 |  | Deficit Flex-1 | 3808.3607 | 5063.9626 | 6319.5645 | 7575.1665 | 8830.7684 | 10086.3703 | 11341.9723 | 10868.4556 | 10394.9389 | 9921.4223 | 10158.1806 | 11732.4477 | 12452.8192 | 13173.1908 | 13893.5623 | 14613.9339 | 15334.3054 | 16054.677 | 16775.0485 | 17495.4201 | 18215.7916 | 18936.1632 | 19656.5347 | 20376.9063 | 21097.2778 | 21817.6494 | 22538.0209
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 15863.8465 | 17648.2938 | 18532.2445 | 19475.1482 | 20493.6788 | 21703.1962 | 22945.9872 | 22121.1674 | 21313.2168 | 20520.3431 | 21799.1819 | 23155.1608 | 24606.2129 | 26062.5347 | 27614.3526 | 29256.497 | 30979.0521 | 32583.3718 | 34238.6898 | 35926.361 | 37681.7452 | 39178.6708 | 40662.7614 | 42131.1117 | 43588.0399 | 44646.03 | 45597.0962
N-0 |  | EENS(Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS(Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 31.9333 | 62.8667 | 93.8 | 225 | 356.2 | 487.4 | 618.6 | 749.8
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17.0667 | 33.1333 | 49.2 | 79.68 | 110.16 | 140.64 | 171.12 | 201.6
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0001 | 0.23539 | 0.47069 | 0.70598 | 4.1389 | 7.5718 | 11.0047 | 14.4377 | 17.8706
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0001 | 0.039288 | 0.078476 | 0.11766 | 0.28224 | 0.44682 | 0.6114 | 0.77598 | 0.94056
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.6667 | 4.3333 | 6 | 8.6 | 11.2 | 13.8 | 16.4 | 19
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13378.6853 | 184613.5432 | 655744.9507 | 1176150.7446 | 1859058.0492 | 2929109.3858 | 3949158.618 | 5053459.3236 | 6408936.1762
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80036.6547 | 1104432.1645 | 3740697.1497 | 6181651.0287 | 8806685.1831 | 13335315.4909 | 17196082.6785 | 21988181.2479 | 28116925.8054
N-1 Monetized | Residential | $ | 1269.4985 | 3507.3999 | 5745.3013 | 7983.2026 | 10221.104 | 12459.0054 | 14696.9068 | 13659.3661 | 11760.7142 | 9813.2626 | 13588.9086 | 17547.2036 | 24911.6828 | 32276.162 | 39640.6412 | 47005.1204 | 54369.5996 | 77256.7859 | 100143.9722 | 123031.1586 | 145918.3449 | 168805.5312 | 204593.5776 | 240381.624 | 276169.6704 | 311957.7168 | 347745.7632
N-1 Monetized | Commercial | $ | 5267.7659 | 14553.906 | 23840.0461 | 33126.1863 | 42412.3264 | 51698.4665 | 60984.6067 | 56679.3462 | 48800.9171 | 40719.9943 | 56386.9837 | 72811.8726 | 103370.6747 | 133929.4768 | 164488.2789 | 195047.081 | 225605.8831 | 320575.9384 | 415545.9936 | 510516.0489 | 605486.1042 | 700456.1595 | 848958.1509 | 997460.1423 | 1145962.1336 | 1294464.125 | 1442966.1164
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 4851883.8074 | 5548866.4784 | 5954619.7491 | 6363793.1776 | 6862681.5292 | 7430776.4174 | 7958064.5941 | 7957168.049 | 7874171.1774 | 7776287.7266 | 8450702.8694 | 9080603.7964 | 9916810.716 | 10742147.0818 | 11532452.8263 | 12410650.1702 | 13427370.4397 | 14508754.4423 | 15576671.5917 | 16678510.3769 | 17727086.4233 | 18931202.4562 | 20126360.6731 | 21277070.9728 | 22513024.6587 | 23603677.4869 | 24710377.8006
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 7386.6021 | Losses (MWh) | 338.8 | 367.499 | 396.1981 | 424.8971 | 453.5962 | 482.2952 | 510.9942 | 609.1846 | 1110.9038 | 1614.3231 | 1563.8673 | 1516.91 | 1469.9526 | 1422.9953 | 1376.038 | 1329.0806 | 1282.1233 | 1235.166 | 1188.2087 | 1141.2513 | 1094.294 | 1047.3367 | 1000.3793 | 953.422 | 906.4647 | 859.5073 | 812.55
| 387169.6632 | Losses ($) | 13552 | 15067.4606 | 16650.2242 | 18302.7088 | 20027.4113 | 21826.9097 | 23703.8658 | 28965.1629 | 54141.1386 | 80642.7325 | 80075.2948 | 79612.6936 | 79076.9153 | 78464.5902 | 77772.2257 | 76996.2027 | 76132.7708 | 75178.0448 | 74127.9994 | 72978.4655 | 71725.1249 | 70363.5058 | 68888.9774 | 67296.7455 | 65581.8464 | 63739.1418 | 61763.3134
N-1 | 114.4291 | EENS | 4.2 | 6.0167 | 6.7133 | 7.41 | 8.1067 | 8.8033 | 9.5 | 5.1 | 5.7 | 5.6 | 5.2 | 13.9667 | 14.0533 | 14.14 | 14.2267 | 14.3133 | 14.4 | 24.21 | 34.02 | 43.83 | 53.64 | 23.6 | 33.3 | 43 | 52.7 | 62.4 | 72.1
N-1 | -30.4126 | IP | -1 | -1.9167 | -2.1533 | -2.39 | -2.6267 | -2.8633 | -3.1 | -3.3 | -3.2 | -3.3 | -3.3 | -3.7667 | -4.1933 | -4.62 | -5.0467 | -5.4733 | -5.9 | -5.96 | -6.02 | -6.08 | -6.14 | -6.2 | -6.1 | -6 | -5.9 | -5.8 | -5.7
N-1 | 54.4087 | SAIDI | 0.068918 | 0.15907 | 0.18883 | 0.21859 | 0.24835 | 0.27811 | 0.30787 | 0.28195 | 0.24759 | 0.28509 | 0.25669 | 0.52331 | 0.49656 | 0.4698 | 0.44305 | 0.4163 | 0.38955 | 16.6918 | 32.994 | 49.2962 | 65.5984 | 81.9007 | 66.2507 | 50.6007 | 34.9507 | 19.3008 | 3.6508
N-1 | 0.65104 | SAIFI | 0.00075996 | 0.0045419 | 0.0038851 | 0.0032282 | 0.0025714 | 0.0019146 | 0.0012578 | -0.0022394 | -0.0012916 | -0.0010002 | -0.00209 | 0.0039543 | 0.002067 | 0.00017976 | -0.0017075 | -0.0035948 | -0.005482 | 0.19896 | 0.4034 | 0.60784 | 0.81228 | 1.0167 | 0.81881 | 0.62089 | 0.42298 | 0.22506 | 0.027145
N-1 | 225.5303 | PFD | 11 | 17.1667 | 18.5333 | 19.9 | 21.2667 | 22.6333 | 24 | 23 | 22 | 23 | 22 | 24.6667 | 26.5333 | 28.4 | 30.2667 | 32.1333 | 34 | 37 | 40 | 43 | 46 | 49 | 49.2 | 49.4 | 49.6 | 49.8 | 50
N-1 | 39141.4455 | Flex-1 | 1637.465 | 2177.331 | 2717.1969 | 3257.0628 | 3796.9288 | 4336.7947 | 4876.6607 | 4751.6881 | 4626.7154 | 3604.0089 | 4264.9845 | 5180.7853 | 5378.55 | 5576.3147 | 5774.0795 | 5971.8442 | 6169.609 | 6367.3737 | 6565.1384 | 6762.9032 | 6960.6679 | 7158.4327 | 7356.1974 | 7553.9621 | 7751.7269 | 7949.4916 | 8147.2564
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 479183.4057 | Flex-2-2 | 41950.3173 | 44543.4531 | 45828.8607 | 47153.3528 | 48574.548 | 50215.7648 | 51874.692 | 50778.1149 | 49693.1357 | 48611.2731 | 50344.583 | 52146.7651 | 54023.4147 | 55888.5229 | 57769.072 | 59689.4741 | 61697.8438 | 63562.3581 | 65462.1684 | 67413.8488 | 69383.773 | 71058.9731 | 72692.9097 | 74263.6867 | 75805.9061 | 76906.7651 | 77904.2708
N-0 | 3422.1306 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1120.76 | 1280.7067 | 1440.6533 | 1600.6 | 1662.4 | 1724.2 | 1786 | 1847.8 | 1909.6
N-0 | 527.3168 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 135.2 | 128.7333 | 122.2667 | 115.8 | 92.16 | 68.52 | 44.88 | 21.24 | -2.4
N-0 | 49.0833 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8068 | 12.0924 | 12.378 | 12.6636 | 26.886 | 41.1084 | 55.3308 | 69.5533 | 83.7757
N-0 | 2.6068 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61653 | 0.50119 | 0.38585 | 0.27051 | 0.57774 | 0.88496 | 1.1922 | 1.4994 | 1.8066
N-0 | 73.8974 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 19 | 20.3333 | 21.6667 | 23 | 22 | 21 | 20 | 19 | 18
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 34143.207 | 85.4671 | -38.5701 | -162.6073 | -286.6445 | -410.6816 | -534.7188 | -658.756 | -1572.2209 | -1299.1265 | -1202.7397 | -1056.4557 | 1671.6039 | 993.4792 | 315.3545 | -362.7701 | -1040.8948 | -1719.0195 | 4040.5972 | 9800.2139 | 15559.8305 | 21319.4472 | 27079.0638 | 37562.4951 | 48045.9264 | 58529.3577 | 69012.789 | 79496.2203
Commerical(N-1) | EENS | 141676.7537 | 354.6443 | -160.0462 | -674.7367 | -1189.4272 | -1704.1177 | -2218.8082 | -2733.4987 | -6523.9084 | -5390.7071 | -4990.7514 | -4383.7478 | 6936.2967 | 4122.428 | 1308.5592 | -1505.3095 | -4319.1782 | -7133.0469 | 16766.4008 | 40665.8485 | 64565.2962 | 88464.7439 | 112364.1916 | 155865.0412 | 199365.8907 | 242866.7403 | 286367.5899 | 329868.4394
Aggregate | EENS | 175819.9607 | 440.1114 | -198.6163 | -837.344 | -1476.0717 | -2114.7993 | -2753.527 | -3392.2547 | -8096.1293 | -6689.8336 | -6193.4911 | -5440.2035 | 8607.9006 | 5115.9072 | 1623.9138 | -1868.0796 | -5360.073 | -8852.0664 | 20806.998 | 50466.0623 | 80125.1267 | 109784.1911 | 139443.2555 | 193427.5363 | 247411.8171 | 301396.098 | 355380.3788 | 409364.6597
Residential (N-0) | EENS | 22277652.2443 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6860802.8013 | 7814963.1205 | 9098538.4333 | 10359467.2322 | 11559971.0849 | 12621132.1128 | 13802655.6389 | 14699632.8299 | 15264592.2233
Commerical(N-0) | EENS | 102260344.9243 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29623484.035 | 33670014.9116 | 38532801.5956 | 44228764.4593 | 50286583.6721 | 55878170.6678 | 62357409.4146 | 67170738.8145 | 70247543.9295
Aggregate | EENS | 124537997.1687 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36484286.8364 | 41484978.0321 | 47631340.0289 | 54588231.6915 | 61846554.757 | 68499302.7806 | 76160065.0535 | 81870371.6444 | 85512136.1528
Residential (N-1) | Value for Flex-1 | 207361752.6799 | 6621897.889 | 9025240.0833 | 11544610.7011 | 14184309.0748 | 16948776.9855 | 19842603.0985 | 22870527.5316 | 22841542.6096 | 22796814.3618 | 18201663.851 | 22078347.207 | 27489608.933 | 29252436.5342 | 31086224.5099 | 32993419.1115 | 34976544.5529 | 37038205.3794 | 39181088.9069 | 41407967.7324 | 43721702.3186 | 46125243.6543 | 48621635.9928 | 51214019.671 | 53905634.0105 | 56699820.3048 | 59600024.8925 | 62609802.3219
Commerical(N-1) | Value for Flex-1 | 854254218.5995 | 27279785.8511 | 37180672.4982 | 47559553.6114 | 58434140.8601 | 69822732.7501 | 81744232.8966 | 94218168.8424 | 94098761.6153 | 93914497.6713 | 74984166.2182 | 90954677.0199 | 113247086.7709 | 120509288.6742 | 128063821.2434 | 135920762.1357 | 144090510.1843 | 152583795.159 | 161411687.8136 | 170585610.2289 | 180117346.4601 | 190019053.4965 | 200303272.5432 | 210982940.6337 | 222071402.5835 | 233582423.2928 | 245530200.411 | 257929377.3705
Aggregate | Value for Flex-1 | 1061615971.2793 | 33901683.7401 | 46205912.5815 | 59104164.3126 | 72618449.9349 | 86771509.7356 | 101586835.9951 | 117088696.374 | 116940304.2249 | 116711312.0331 | 93185830.0692 | 113033024.2269 | 140736695.704 | 149761725.2085 | 159150045.7534 | 168914181.2472 | 179067054.7372 | 189622000.5384 | 200592776.7205 | 211993577.9613 | 223839048.7787 | 236144297.1508 | 248924908.536 | 262196960.3047 | 275977036.594 | 290282243.5976 | 305130225.3035 | 320539179.6924
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 158850774.4516 | 11220634.2188 | 12144918.1584 | 12786910.2509 | 13549003.8391 | 14198581.0583 | 15000915.7058 | 15909014.2717 | 15943271.5953 | 15999716.4072 | 16077364.9697 | 17017237.4897 | 18089024.9798 | 19073573.1791 | 20183246.8534 | 21490829.7021 | 22579839.7873 | 23724942.3552 | 24911056.9306 | 26196805.9595 | 27625844.3348 | 29110039.0485 | 30411440.883 | 31944711.5843 | 33332991.3303 | 34748837.6652 | 36032493.5279 | 37232773.5323
Aggregate ($M) |  | 1345.1806 | 46186416.015 | 61030693.7386 | 75823553.0558 | 91447167.7399 | 107619710.7541 | 123194795.4827 | 142105261.8508 | 140635817.5108 | 139232771.3537 | 116937348.717 | 137617805.6599 | 169574939.7199 | 182678413.1563 | 194931145.2106 | 207214698.4501 | 222706912.1605 | 239510927.0138 | 255387446.2078 | 274725136.8195 | 293029996.2724 | 312995460.4193 | 334064024.3659 | 356181654.1822 | 378056742.522 | 401492542.4143 | 423388470.8547 | 443693454.0373
Aggregate ($M)+ Monetized Losses |  | 1345.5677 | 46199968.015 | 61045761.1992 | 75840203.28 | 91465470.4487 | 107639738.1653 | 123216622.3923 | 142128965.7166 | 140664782.6737 | 139286912.4923 | 117017991.4495 | 137697880.9547 | 169654552.4135 | 182757490.0717 | 195009609.8008 | 207292470.6758 | 222783908.3632 | 239587059.7847 | 255462624.2526 | 274799264.8189 | 293102974.7379 | 313067185.5442 | 334134387.8716 | 356250543.1597 | 378124039.2675 | 401558124.2606 | 423452209.9965 | 443755217.3506
Project Cost |  | 185
Benefit-Cost Ratio |  | 7.2733
Market Participation Revenue (All costs are $x1,000) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Menifee
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Menifee | Losses (MWh) | 48898.025 | 49299.6596 | 49701.2942 | 50102.9288 | 50504.5635 | 50906.1981 | 51307.8327 | 50631.55 | 50425.7 | 51306.3471 | 50213.5 | 50566.1188 | 50918.7375 | 51271.3563 | 51623.975 | 51976.5938 | 52329.2125 | 52681.8313 | 53034.45 | 53387.0688 | 53739.6875 | 54092.3063 | 54444.925 | 54797.5438 | 55150.1625 | 55502.7813 | 55855.4
N-1 |  | EENS | 5.8 | 14.4833 | 23.1667 | 31.85 | 40.5333 | 49.2167 | 57.9 | 52.5 | 44.1 | 35.9 | 48.5 | 61.1 | 82.38 | 103.66 | 124.94 | 146.22 | 167.5 | 220.02 | 272.54 | 325.06 | 377.58 | 430.1 | 490.7 | 551.3 | 611.9 | 672.5 | 733.1
N-1 |  | IP | 3 | 4.9167 | 6.8333 | 8.75 | 10.6667 | 12.5833 | 14.5 | 13.5 | 11.8 | 10.1 | 12.9 | 15.1 | 17.26 | 19.42 | 21.58 | 23.74 | 25.9 | 27.82 | 29.74 | 31.66 | 33.58 | 35.5 | 36.58 | 37.66 | 38.74 | 39.82 | 40.9
N-1 |  | SAIDI | 0.015894 | 0.083764 | 0.15163 | 0.2195 | 0.28737 | 0.35524 | 0.42311 | 0.33569 | 0.28198 | 0.19676 | 0.31012 | 0.4465 | 0.87624 | 1.306 | 1.7357 | 2.1655 | 2.5952 | 4.3788 | 6.1623 | 7.9458 | 9.7293 | 11.5128 | 14.8115 | 18.1102 | 21.4089 | 24.7076 | 28.0063
N-1 |  | SAIFI | 0.005298 | 0.01323 | 0.021162 | 0.029094 | 0.037025 | 0.044957 | 0.052889 | 0.047956 | 0.040283 | 0.032793 | 0.044303 | 0.055812 | 0.075253 | 0.094694 | 0.11414 | 0.13358 | 0.15302 | 0.20155 | 0.25009 | 0.29862 | 0.34715 | 0.39569 | 0.45221 | 0.50874 | 0.56527 | 0.62179 | 0.67832
N-1 |  | PFD | 3 | 3.8333 | 4.6667 | 5.5 | 6.3333 | 7.1667 | 8 | 7 | 7 | 6 | 7 | 8 | 9.8 | 11.6 | 13.4 | 15.2 | 17 | 19.6 | 22.2 | 24.8 | 27.4 | 30 | 32.8 | 35.6 | 38.4 | 41.2 | 44
N-1 |  | Deficit Flex-1 | 3808.3607 | 5063.9626 | 6319.5645 | 7575.1665 | 8830.7684 | 10086.3703 | 11341.9723 | 10868.4556 | 10394.9389 | 9921.4223 | 10158.1806 | 11732.4477 | 12452.8192 | 13173.1908 | 13893.5623 | 14613.9339 | 15334.3054 | 16054.677 | 16775.0485 | 17495.4201 | 18215.7916 | 18936.1632 | 19656.5347 | 20376.9063 | 21097.2778 | 21817.6494 | 22538.0209
N-1 |  | Deficit Flex-2-1 | 71622.0596 | 73607.6578 | 74550.3716 | 75519.1611 | 76537.9646 | 77706.0976 | 78873.9457 | 78104.0722 | 77334.1987 | 76564.1828 | 77797.5762 | 79065.0248 | 80369.2357 | 81649.3659 | 82957.2816 | 84288.8506 | 85651.4825 | 86890.5755 | 88135.2257 | 89379.4484 | 90631.6505 | 91676.5296 | 92696.758 | 93682.9313 | 94642.0315 | 95326.5535 | 95938.263
N-1 |  | Deficit Flex-2-2 | 15863.8465 | 17648.2938 | 18532.2445 | 19475.1482 | 20493.6788 | 21703.1962 | 22945.9872 | 22121.1674 | 21313.2168 | 20520.3431 | 21799.1819 | 23155.1608 | 24606.2129 | 26062.5347 | 27614.3526 | 29256.497 | 30979.0521 | 32583.3718 | 34238.6898 | 35926.361 | 37681.7452 | 39178.6708 | 40662.7614 | 42131.1117 | 43588.0399 | 44646.03 | 45597.0962
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 1160.0589 | 3691.1856 | 6222.3122 | 8753.4388 | 11284.5654 | 13815.692 | 16346.8187 | 14543.9727 | 12267.4117 | 11508.0322 | 11795.733 | 19011.8638 | 26614.4348 | 34217.0058 | 41819.5768 | 49422.1478 | 57024.7188 | 78728.887 | 100433.0553 | 122137.2235 | 143841.3918 | 165545.56 | 204593.3511 | 243641.1422 | 282688.9333 | 321736.7244 | 360784.5155
N-1 Monetized | Commercial | $ | 4813.6481 | 15316.5222 | 25819.3962 | 36322.2702 | 46825.1443 | 57328.0183 | 67830.8924 | 60350.0086 | 50903.4509 | 47752.4167 | 48946.2271 | 78889.4593 | 110436.22 | 141982.9806 | 173529.7412 | 205076.5019 | 236623.2625 | 326684.4011 | 416745.5396 | 506806.6782 | 596867.8168 | 686928.9554 | 848957.2112 | 1010985.467 | 1173013.7229 | 1335041.9787 | 1497070.2345
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 4851883.8074 | 5548866.4784 | 5954619.7491 | 6363793.1776 | 6862681.5292 | 7430776.4174 | 7958064.5941 | 7957168.049 | 7874171.1774 | 7776287.7266 | 8450702.8694 | 9080603.7964 | 9916810.716 | 10742147.0818 | 11532452.8263 | 12410650.1702 | 13427370.4397 | 14508754.4423 | 15576671.5917 | 16678510.3769 | 17727086.4233 | 18931202.4562 | 20126360.6731 | 21277070.9728 | 22513024.6587 | 23603677.4869 | 24710377.8006
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 11889.763 | Losses (MWh) | 768.975 | 804.1308 | 839.2865 | 874.4423 | 909.5981 | 944.7538 | 979.9096 | 1066.6346 | 1562.6538 | 972.176 | 2355.1923 | 2292.7428 | 2230.2933 | 2167.8437 | 2105.3942 | 2042.9447 | 1980.4952 | 1918.0457 | 1855.5962 | 1793.1466 | 1730.6971 | 1668.2476 | 1605.7981 | 1543.3486 | 1480.899 | 1418.4495 | 1356
| 614918.6288 | Losses ($) | 30759 | 32969.3615 | 35271.0168 | 37667.1489 | 40161.0433 | 42756.0904 | 45455.7893 | 50715.7349 | 76157.679 | 48564.5823 | 120593.8109 | 120331.0889 | 119979.8597 | 119535.8621 | 118994.6772 | 118351.7232 | 117602.2498 | 116741.3329 | 115763.8687 | 114664.568 | 113437.9499 | 112078.3354 | 110579.8416 | 108936.3741 | 107141.6208 | 105189.0446 | 103071.8761
N-1 | 114.4291 | EENS | 4.2 | 6.0167 | 6.7133 | 7.41 | 8.1067 | 8.8033 | 9.5 | 5.1 | 5.7 | 5.6 | 5.2 | 13.9667 | 14.0533 | 14.14 | 14.2267 | 14.3133 | 14.4 | 24.21 | 34.02 | 43.83 | 53.64 | 23.6 | 33.3 | 43 | 52.7 | 62.4 | 72.1
N-1 | -30.4126 | IP | -1 | -1.9167 | -2.1533 | -2.39 | -2.6267 | -2.8633 | -3.1 | -3.3 | -3.2 | -3.3 | -3.3 | -3.7667 | -4.1933 | -4.62 | -5.0467 | -5.4733 | -5.9 | -5.96 | -6.02 | -6.08 | -6.14 | -6.2 | -6.1 | -6 | -5.9 | -5.8 | -5.7
N-1 | 54.4087 | SAIDI | 0.068918 | 0.15907 | 0.18883 | 0.21859 | 0.24835 | 0.27811 | 0.30787 | 0.28195 | 0.24759 | 0.28509 | 0.25669 | 0.52331 | 0.49656 | 0.4698 | 0.44305 | 0.4163 | 0.38955 | 16.6918 | 32.994 | 49.2962 | 65.5984 | 81.9007 | 66.2507 | 50.6007 | 34.9507 | 19.3008 | 3.6508
N-1 | 0.65104 | SAIFI | 0.00075996 | 0.0045419 | 0.0038851 | 0.0032282 | 0.0025714 | 0.0019146 | 0.0012578 | -0.0022394 | -0.0012916 | -0.0010002 | -0.00209 | 0.0039543 | 0.002067 | 0.00017976 | -0.0017075 | -0.0035948 | -0.005482 | 0.19896 | 0.4034 | 0.60784 | 0.81228 | 1.0167 | 0.81881 | 0.62089 | 0.42298 | 0.22506 | 0.027145
N-1 | 225.5303 | PFD | 11 | 17.1667 | 18.5333 | 19.9 | 21.2667 | 22.6333 | 24 | 23 | 22 | 23 | 22 | 24.6667 | 26.5333 | 28.4 | 30.2667 | 32.1333 | 34 | 37 | 40 | 43 | 46 | 49 | 49.2 | 49.4 | 49.6 | 49.8 | 50
N-1 | 39141.4455 | Flex-1 | 1637.465 | 2177.331 | 2717.1969 | 3257.0628 | 3796.9288 | 4336.7947 | 4876.6607 | 4751.6881 | 4626.7154 | 3604.0089 | 4264.9845 | 5180.7853 | 5378.55 | 5576.3147 | 5774.0795 | 5971.8442 | 6169.609 | 6367.3737 | 6565.1384 | 6762.9032 | 6960.6679 | 7158.4327 | 7356.1974 | 7553.9621 | 7751.7269 | 7949.4916 | 8147.2564
N-1 | 1132819.4222 | Flex-2-1 | 121242.6066 | 121631.5842 | 121816.3938 | 122006.2144 | 122205.9593 | 122434.8408 | 122663.7646 | 122512.8227 | 122361.9505 | 122211.0504 | 122452.7587 | 122701.1407 | 122956.7271 | 123207.5943 | 123463.9067 | 123724.8544 | 123991.8895 | 124234.7147 | 124478.6289 | 124722.4593 | 124967.8535 | 125172.6186 | 125372.5528 | 125565.8133 | 125753.7683 | 125887.9141 | 126007.7909
| 479183.4057 | Flex-2-2 | 41950.3173 | 44543.4531 | 45828.8607 | 47153.3528 | 48574.548 | 50215.7648 | 51874.692 | 50778.1149 | 49693.1357 | 48611.2731 | 50344.583 | 52146.7651 | 54023.4147 | 55888.5229 | 57769.072 | 59689.4741 | 61697.8438 | 63562.3581 | 65462.1684 | 67413.8488 | 69383.773 | 71058.9731 | 72692.9097 | 74263.6867 | 75805.9061 | 76906.7651 | 77904.2708
N-0 | 3662.4319 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 | 603.3371 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 | 54.0898 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 | 2.9079 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 | 81.9765 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 24991.4224 | 194.9066 | -222.3558 | -639.6182 | -1056.8806 | -1474.143 | -1891.4054 | -2308.6678 | -2456.8275 | -1805.824 | -2897.5093 | 736.7199 | 206.9437 | -709.2728 | -1625.4892 | -2541.7057 | -3457.9222 | -4374.1387 | 2568.4961 | 9511.1308 | 16453.7655 | 23396.4003 | 30339.035 | 37562.7216 | 44786.4082 | 52010.0947 | 59233.7813 | 66457.4679
Commerical(N-1) | EENS | 103701.5532 | 808.7621 | -922.6623 | -2654.0867 | -4385.5112 | -6116.9356 | -7848.36 | -9579.7844 | -10194.5708 | -7493.2409 | -12023.1738 | 3057.0088 | 858.7099 | -2943.1173 | -6744.9446 | -10546.7718 | -14348.5991 | -18150.4263 | 10657.9381 | 39466.3025 | 68274.6669 | 97083.0313 | 125891.3958 | 155865.9809 | 185840.566 | 215815.1511 | 245789.7362 | 275764.3213
Aggregate | EENS | 128692.9756 | 1003.6687 | -1145.0182 | -3293.705 | -5442.3918 | -7591.0786 | -9739.7654 | -11888.4522 | -12651.3983 | -9299.0649 | -14920.6831 | 3793.7287 | 1065.6536 | -3652.3901 | -8370.4338 | -13088.4775 | -17806.5213 | -22524.565 | 13226.4341 | 48977.4333 | 84728.4324 | 120479.4316 | 156230.4307 | 193428.7024 | 230626.9741 | 267825.2458 | 305023.5175 | 342221.7892
Residential (N-0) | EENS | 24322736.8672 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21673528.3995
Commerical(N-0) | EENS | 111616614.0139 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98364469.7349
Aggregate | EENS | 135939350.8811 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 120037998.1344
Residential (N-1) | Value for Flex-1 | 207361752.6799 | 6621897.889 | 9025240.0833 | 11544610.7011 | 14184309.0748 | 16948776.9855 | 19842603.0985 | 22870527.5316 | 22841542.6096 | 22796814.3618 | 18201663.851 | 22078347.207 | 27489608.933 | 29252436.5342 | 31086224.5099 | 32993419.1115 | 34976544.5529 | 37038205.3794 | 39181088.9069 | 41407967.7324 | 43721702.3186 | 46125243.6543 | 48621635.9928 | 51214019.671 | 53905634.0105 | 56699820.3048 | 59600024.8925 | 62609802.3219
Commerical(N-1) | Value for Flex-1 | 854254218.5995 | 27279785.8511 | 37180672.4982 | 47559553.6114 | 58434140.8601 | 69822732.7501 | 81744232.8966 | 94218168.8424 | 94098761.6153 | 93914497.6713 | 74984166.2182 | 90954677.0199 | 113247086.7709 | 120509288.6742 | 128063821.2434 | 135920762.1357 | 144090510.1843 | 152583795.159 | 161411687.8136 | 170585610.2289 | 180117346.4601 | 190019053.4965 | 200303272.5432 | 210982940.6337 | 222071402.5835 | 233582423.2928 | 245530200.411 | 257929377.3705
Aggregate | Value for Flex-1 | 1061615971.2793 | 33901683.7401 | 46205912.5815 | 59104164.3126 | 72618449.9349 | 86771509.7356 | 101586835.9951 | 117088696.374 | 116940304.2249 | 116711312.0331 | 93185830.0692 | 113033024.2269 | 140736695.704 | 149761725.2085 | 159150045.7534 | 168914181.2472 | 179067054.7372 | 189622000.5384 | 200592776.7205 | 211993577.9613 | 223839048.7787 | 236144297.1508 | 248924908.536 | 262196960.3047 | 275977036.594 | 290282243.5976 | 305130225.3035 | 320539179.6924
Residential (N-1) | Value for Flex-2 | 47590346.8566 | 4137768.8918 | 4254820.0219 | 4367817.0089 | 4483988.7467 | 4603613.04 | 4727541.1018 | 4854789.9826 | 4970036.4015 | 5088013.7948 | 5208782.5949 | 5349561.6042 | 5494422.9196 | 5643514.492 | 5796404.6138 | 5953674.6205 | 6115414.4884 | 6281828.7096 | 6451484.2915 | 6625754.4764 | 6804701.4224 | 6988542.0673 | 7174992.9141 | 7366114.6358 | 7561906.16 | 7762555.9387 | 7965107.4351 | 8172009.5151
Commerical(N-1) | Value for Flex-2 | 214520720.019 | 18651622.032 | 19179247.7873 | 19688598.8768 | 20212260.6376 | 20751485.317 | 21310109.8871 | 21883703.5531 | 22403194.2985 | 22934995.3263 | 23479379.0442 | 24113961.8205 | 24766946.2118 | 25438999.1296 | 26128174.586 | 26837093.039 | 27566160.0707 | 28316297.4599 | 29081045.7754 | 29866595.115 | 30673225.6658 | 31501915.308 | 32342370.8321 | 33203881.0342 | 34086441.0812 | 34990900.448 | 35903932.0968 | 36836574.6623
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 262111066.8756 | 22789390.9238 | 23434067.8092 | 24056415.8857 | 24696249.3843 | 25355098.357 | 26037650.9889 | 26738493.5357 | 27373230.7 | 28023009.1211 | 28688161.6391 | 29463523.4247 | 30261369.1314 | 31082513.6216 | 31924579.1999 | 32790767.6595 | 33681574.5591 | 34598126.1695 | 35532530.0669 | 36492349.5914 | 37477927.0882 | 38490457.3753 | 39517363.7461 | 40569995.67 | 41648347.2412 | 42753456.3867 | 43869039.5319 | 45008584.1774
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 158850774.4516 | 11220634.2188 | 12144918.1584 | 12786910.2509 | 13549003.8391 | 14198581.0583 | 15000915.7058 | 15909014.2717 | 15943271.5953 | 15999716.4072 | 16077364.9697 | 17017237.4897 | 18089024.9798 | 19073573.1791 | 20183246.8534 | 21490829.7021 | 22579839.7873 | 23724942.3552 | 24911056.9306 | 26196805.9595 | 27625844.3348 | 29110039.0485 | 30411440.883 | 31944711.5843 | 33332991.3303 | 34748837.6652 | 36032493.5279 | 37232773.5323
Aggregate ($M) |  | 1618.6459 | 68976370.4961 | 84463815.146 | 99877512.5805 | 116139450.804 | 132969332.8318 | 149225460.2332 | 168835259.1889 | 168004492.9418 | 167253171.2435 | 145616783.1641 | 167090563.0168 | 199828766.6043 | 213752158.4807 | 226845730.0628 | 239994245.7116 | 256376040.2713 | 274095380.6847 | 290912395.7109 | 311309413.1219 | 331801572.374 | 355893055.1356 | 380955977.0606 | 407417394.2506 | 435952729.7968 | 465357669.2453 | 494248794.0968 | 523160757.3258
Aggregate ($M)+ Monetized Losses |  | 1619.2608 | 69007129.4961 | 84496784.5075 | 99912783.5972 | 116177117.9529 | 133009493.8751 | 149268216.3236 | 168880714.9782 | 168055208.6767 | 167329328.9225 | 145665347.7464 | 167211156.8277 | 199949097.6932 | 213872138.3404 | 226965265.925 | 240113240.3888 | 256494391.9945 | 274212982.9345 | 291029137.0438 | 311425176.9906 | 331916236.9421 | 356006493.0854 | 381068055.3961 | 407527974.0922 | 436061666.1709 | 465464810.866 | 494353983.1413 | 523263829.2019
Project Cost |  | 315
Benefit-Cost Ratio |  | 5.1405

## Mira Loma
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Mira Loma | Losses (MWh) | 48453.3 | 48868.5423 | 49283.7846 | 49699.0269 | 50114.2692 | 50529.5115 | 50805.9144 | 50242.6 | 50024.2 | 49809.375 | 50155 | 50497.7984 | 50840.5969 | 51183.3953 | 51526.1937 | 51868.9922 | 52211.7906 | 52554.5891 | 52897.3875 | 53240.1859 | 53582.9844 | 53925.7828 | 54268.5813 | 54611.3797 | 54954.1781 | 55296.9766 | 55639.775
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 29.4 | 22.7 | 17.3 | 15 | 20.5 | 26.6 | 44.4667 | 56.45 | 68.4333 | 80.4167 | 92.4 | 133.26 | 174.12 | 214.98 | 255.84 | 296.7 | 347.96 | 399.22 | 450.48 | 501.74 | 553
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.8 | 7.2 | 5.5 | 8.3 | 10.5 | 12.2333 | 14.2 | 16.1667 | 18.1333 | 20.1 | 22.94 | 25.78 | 28.62 | 31.46 | 34.3 | 47.88 | 61.46 | 75.04 | 88.62 | 102.2
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0.15146 | 0.093554 | 0.071299 | 0.06182 | 0.084487 | 0.13703 | 0.36345 | 0.50293 | 0.64241 | 0.7819 | 0.92138 | 1.9586 | 2.9957 | 4.0329 | 5.0701 | 6.1073 | 5.9306 | 5.7539 | 5.5773 | 5.4006 | 5.2239
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0.030292 | 0.023388 | 0.017825 | 0.015455 | 0.021122 | 0.027407 | 0.04579 | 0.058125 | 0.070459 | 0.082793 | 0.095128 | 0.13661 | 0.1781 | 0.21959 | 0.26107 | 0.30256 | 0.34652 | 0.39049 | 0.43446 | 0.47842 | 0.52239
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 4 | 4 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 12.8 | 15.6 | 18.4 | 21.2 | 24 | 21.2 | 18.4 | 15.6 | 12.8 | 10
N-1 |  | Deficit Flex-1 | 2180.0835 | 2898.8487 | 3617.6139 | 4336.3791 | 5055.1443 | 5773.9095 | 6492.6746 | 6092.5267 | 5692.3787 | 5292.2308 | 5708 | 5964.2406 | 6199.164 | 6534.0874 | 6869.0108 | 7203.9342 | 7538.8575 | 7873.7809 | 8208.7043 | 8543.6277 | 8878.551 | 9213.4744 | 9548.3978 | 9883.3212 | 10218.2445 | 10553.1679 | 10888.0913
N-1 |  | Deficit Flex-2-1 | 139482.7176 | 141661.1434 | 142695.4071 | 143758.2787 | 144876.0214 | 146157.5954 | 147438.8568 | 146594.2185 | 145749.5803 | 144904.7857 | 146257.9578 | 147648.4922 | 149079.3591 | 150483.8067 | 151918.7381 | 153379.6199 | 154874.5812 | 156234.0064 | 157599.5284 | 158964.5814 | 160338.3887 | 161484.7393 | 162604.0453 | 163685.9889 | 164738.2303 | 165489.2283 | 166160.3429
N-1 |  | Deficit Flex-2-2 | 18207.4584 | 20177.9506 | 21154.9937 | 22187.8326 | 23306.0057 | 24628.6125 | 25977.651 | 25085.8101 | 24204.4899 | 23335.3402 | 24733.5106 | 26201.7967 | 27781.6878 | 29389.983 | 31072.602 | 32829.5502 | 34677.1444 | 36397.4901 | 38187.068 | 40009.7945 | 41888.713 | 43498.5243 | 45101.3841 | 46679.9631 | 48252.2118 | 49385.5978 | 50403.8917
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4667 | 38.9333 | 58.4 | 101.24 | 144.08 | 186.92 | 229.76 | 272.6 | 323.24 | 373.88 | 424.52 | 475.16 | 525.8
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1333 | 16.2667 | 24.4 | 33.24 | 42.08 | 50.92 | 59.76 | 68.6 | 91.72 | 114.84 | 137.96 | 161.08 | 184.2
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077362 | 0.15472 | 0.23209 | 0.56483 | 0.89758 | 1.2303 | 1.5631 | 1.8958 | 12.8714 | 23.8469 | 34.8224 | 45.798 | 56.7735
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01934 | 0.038681 | 0.058021 | 0.10058 | 0.14315 | 0.18571 | 0.22827 | 0.27083 | 0.59516 | 0.91948 | 1.2438 | 1.5681 | 1.8925
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3333 | 2.6667 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 11.6 | 16.2 | 20.8 | 25.4 | 30
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85729.7677 | 291859.8125 | 525790.7457 | 891961.6247 | 1277735.2687 | 1685681.2469 | 1831570.6132 | 2374514.3751 | 2863457.2677 | 3462670.4988 | 3789427.1581 | 4289968.8625 | 4338577.7327
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483083.3486 | 1644616.7916 | 2760667.1544 | 4734841.1841 | 6814756.3944 | 8849543.1408 | 8658777.6305 | 11404951.5648 | 13894061.4768 | 16886443.8992 | 17666725.9147 | 20073873.1534 | 19076098.2584
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 7462.6781 | 5906.0497 | 4613.6135 | 4100.249 | 5743.7655 | 10222.7156 | 14701.6657 | 19180.6158 | 23659.5659 | 28138.516 | 32617.4661 | 56047.5316 | 79477.5972 | 102907.6628 | 126337.7283 | 149767.7939 | 190109.2383 | 230450.6826 | 270792.127 | 311133.5713 | 351475.0157
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 30966.277 | 33256.8243 | 35547.3716 | 37837.9189 | 23833.6735 | 42419.0135 | 61004.3534 | 79589.6934 | 98175.0334 | 116760.3733 | 135345.7133 | 232568.4383 | 329791.1633 | 427013.8884 | 524236.6134 | 621459.3385 | 788855.5901 | 956251.8418 | 1123648.0935 | 1291044.3452 | 1458440.5968
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 5590035.4665 | 6282480.6097 | 6730600.6141 | 7226584.158 | 7694667.9842 | 8351447.6567 | 9003229.9816 | 8936987.4783 | 8835154.9115 | 8718533.6489 | 9475291.797 | 10279986.071 | 11008354.5464 | 11873656.1194 | 12823609.0576 | 13920427.5528 | 14970916.7674 | 15974526.1049 | 17110540.9974 | 18367408.4345 | 19668025.4546 | 20858191.3676 | 22155954.9722 | 23377469.9551 | 24675632.6746 | 25884999.8838 | 27123865.2689
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 15238.5981 | Losses (MWh) | 1213.7 | 1235.2481 | 1256.7962 | 1278.3442 | 1299.8923 | 1321.4404 | 1481.8279 | 1455.5846 | 1964.1538 | 2469.1481 | 2413.6923 | 2361.0631 | 2308.4339 | 2255.8047 | 2203.1755 | 2150.5463 | 2097.9171 | 2045.2879 | 1992.6587 | 1940.0294 | 1887.4002 | 1834.771 | 1782.1418 | 1729.5126 | 1676.8834 | 1624.2542 | 1571.625
| 771017.4899 | Losses ($) | 48548 | 50645.1712 | 52816.8584 | 55065.4767 | 57393.5154 | 59803.5402 | 68738.6418 | 69209.3078 | 95725.2295 | 123345.104 | 123589.2087 | 123916.7757 | 124183.4778 | 124386.0671 | 124521.1711 | 124585.289 | 124574.7871 | 124485.8943 | 124314.6976 | 124057.1374 | 123709.0025 | 123265.9252 | 122723.3758 | 122076.6578 | 121320.9018 | 120451.06 | 119461.9006
N-1 | 503.7157 | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 38 | 30.425 | 24.85 | 18.775 | 33.2 | 42.5833 | 51.9667 | 61.35 | 70.7333 | 80.1167 | 89.5 | 110.97 | 132.44 | 153.91 | 175.38 | 157 | 176.04 | 195.08 | 214.12 | 233.16 | 252.2
N-1 | 24.5703 | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 1.4 | 0.625 | -0.55 | -1.925 | 1.3 | 1.0667 | 0.83333 | 0.6 | 0.36667 | 0.13333 | -0.1 | 0.2 | 0.5 | 0.8 | 1.1 | 1.4 | 0.94 | 0.48 | 0.02 | -0.44 | -0.9
N-1 | 64.2375 | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.57952 | 0.48293 | 0.41161 | 0.38062 | 0.48232 | 0.74583 | 1.0093 | 1.2729 | 1.5364 | 1.7999 | 2.0634 | 19.112 | 36.1605 | 53.2091 | 70.2577 | 87.3062 | 73.1946 | 59.083 | 44.9714 | 30.8598 | 16.7482
N-1 | 0.95698 | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.023855 | 0.017718 | 0.013285 | 0.0083786 | 0.021091 | 0.02631 | 0.03153 | 0.036749 | 0.041969 | 0.047188 | 0.052408 | 0.2639 | 0.47539 | 0.68688 | 0.89837 | 1.1099 | 0.91754 | 0.72523 | 0.53291 | 0.3406 | 0.14828
N-1 | 268.006 | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 27 | 25.25 | 24.5 | 24.75 | 25 | 27.6667 | 30.3333 | 33 | 35.6667 | 38.3333 | 41 | 43.8 | 46.6 | 49.4 | 52.2 | 55 | 56 | 57 | 58 | 59 | 60
N-1 | 83412.309 | Flex-1 | 3265.7422 | 4342.4449 | 5419.1475 | 6495.8502 | 7572.5529 | 8649.2556 | 9725.9583 | 9527.617 | 9329.2756 | 8233.2004 | 8715.1651 | 10948.9923 | 11632.2052 | 12215.4181 | 12798.631 | 13381.844 | 13965.0569 | 14548.2698 | 15131.4827 | 15714.6956 | 16297.9085 | 16881.1214 | 17464.3343 | 18047.5472 | 18630.7602 | 19213.9731 | 19797.186
N-1 | 499595.179 | Flex-2-1 | 53381.9486 | 53578.0986 | 53671.3584 | 53767.0968 | 53867.9025 | 53983.343 | 54098.8535 | 54022.6764 | 53946.569 | 53870.4476 | 53992.3771 | 54117.6733 | 54246.6037 | 54373.1535 | 54502.4502 | 54634.0851 | 54768.7908 | 54891.2838 | 55014.3262 | 55137.3263 | 55261.1153 | 55364.4089 | 55465.2656 | 55562.7558 | 55657.5695 | 55725.2393 | 55785.7111
N-1 | 451168.6674 | Flex-2-2 | 39606.7054 | 42013.7963 | 43206.1115 | 44440.6684 | 45762.221 | 47290.3485 | 48843.0282 | 47813.4722 | 46801.8627 | 45796.276 | 47410.2544 | 49100.1292 | 50847.9397 | 52561.0746 | 54310.8226 | 56116.4209 | 57999.7515 | 59748.2398 | 61513.7902 | 63330.4153 | 65176.8052 | 66739.1196 | 68254.2869 | 69714.8354 | 71141.7342 | 72167.1972 | 73097.4753
N-0 | 3157.218 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 221 | 189.425 | 157.65 | 128.475 | 182.1 | 259.6833 | 337.2667 | 414.85 | 492.4333 | 570.0167 | 647.6 | 797.62 | 947.64 | 1097.66 | 1247.68 | 1397.7 | 1539.44 | 1681.18 | 1822.92 | 1964.66 | 2106.4
N-0 | 493.8907 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 89 | 90.8 | 92.6 | 93.36 | 94.12 | 94.88 | 95.64 | 96.4 | 80.12 | 63.84 | 47.56 | 31.28 | 15
N-0 | 37.8706 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.5995 | 9.0662 | 10.533 | 10.7211 | 10.9093 | 11.0974 | 11.2856 | 11.4737 | 18.1535 | 24.8333 | 31.5131 | 38.1929 | 44.8728
N-0 | 2.1996 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.56473 | 0.63782 | 0.71091 | 0.5922 | 0.47349 | 0.35477 | 0.23606 | 0.11734 | 0.26483 | 0.41231 | 0.55979 | 0.70727 | 0.85475
N-0 | 74.7266 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 10.3333 | 10.1667 | 10 | 12.4 | 14.8 | 17.2 | 19.6 | 22 | 24 | 28 | 32 | 34 | 39
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kwh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kwh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kwh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kwh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 115708.5384 | 1354.9655 | 3468.8297 | 5582.694 | 7696.5582 | 9810.4224 | 11924.2866 | 6575.4728 | 6181.0955 | 5847.9742 | 4510.2739 | 6788.6875 | 8996.0919 | 11203.4963 | 13410.9008 | 15618.3052 | 17825.7096 | 20033.1141 | 25249.8515 | 30466.5889 | 35683.3263 | 40900.0637 | 46116.8011 | 52046.8344 | 57976.8678 | 63906.9011 | 69836.9344 | 75766.9677
Commerical(N-1) | EENS | 461063.9862 | 5622.4102 | 14393.8598 | 23165.3095 | 31936.7591 | 40708.2087 | 49479.6583 | 27284.831 | 16898.6135 | 7862.8385 | -2108.676 | 28169.5624 | 37329.1558 | 46488.7492 | 55648.3426 | 64807.936 | 73967.5294 | 83127.1229 | 104773.9008 | 126420.6788 | 148067.4568 | 169714.2347 | 191361.0127 | 215967.6019 | 240574.1912 | 265180.7804 | 289787.3697 | 314393.9589
Aggregate | EENS | 576772.5246 | 6977.3757 | 17862.6896 | 28748.0034 | 39633.3173 | 50518.6311 | 61403.9449 | 33860.3038 | 23079.709 | 13710.8127 | 2401.5979 | 34958.2498 | 46325.2477 | 57692.2455 | 69059.2434 | 80426.2412 | 91793.2391 | 103160.2369 | 130023.7523 | 156887.2677 | 183750.783 | 210614.2984 | 237477.8138 | 268014.4364 | 298551.059 | 329087.6815 | 359624.3041 | 390160.9267
Residential (N-0) | EENS | 21263585.4623 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3027229.6243 | 3574170.2356 | 4274252.6308 | 4713394.8728 | 5596446.218 | 6313895.4168 | 7922712.7708 | 9161103.6017 | 10555571.8664 | 12087570.9998 | 13962387.0988 | 15463123.2909 | 17334950.6668
Commerical(N-0) | EENS | 96708426.1877 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13215512.8397 | 15554730.8693 | 18612125.6557 | 19522607.8773 | 22888764.2953 | 25924903.9353 | 33614721.1148 | 39005463.9232 | 45199207.3783 | 52327042.2594 | 61886766.1784 | 69085046.9091 | 79288371.4766
Aggregate | EENS | 117972011.6501 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16242742.464 | 19128901.1049 | 22886378.2865 | 24236002.75 | 28485210.5134 | 32238799.3522 | 41537433.8857 | 48166567.5249 | 55754779.2447 | 64414613.2592 | 75849153.2772 | 84548170.2 | 96623322.1434
Residential (N-1) | Value for Flex-1 | 447270038.4836 | 13206640.1538 | 17999839.333 | 23024444.3211 | 28289029.659 | 33802453.9861 | 39573868.886 | 45612727.9971 | 45799611.9601 | 45967332.1661 | 41580903.7386 | 45115390.6724 | 58096118.9648 | 63264326.8193 | 68097166.019 | 73132106.9744 | 78376234.2488 | 83836860.3201 | 89521532.5485 | 95438040.3507 | 101594422.5851 | 107998975.156 | 114660258.8414 | 121587107.3516 | 128788635.6254 | 136274248.3709 | 144053648.8564 | 152136847.961
Commerical(N-1) | Value for Flex-1 | 1842588193.2897 | 54406504.1844 | 74152723.3715 | 94852249.4528 | 116540406.3861 | 139253688.5102 | 163029796.9864 | 187907677.3312 | 188677570.5812 | 189368516.1955 | 171298043.0229 | 185858830.3174 | 239334660.6524 | 260625777.7714 | 280535299.2757 | 301277405.7441 | 322881282.9739 | 345377055.6865 | 368795816.233 | 393169654.1469 | 418531686.5714 | 444916089.5833 | 472358130.4417 | 500894200.787 | 530561850.8181 | 561399824.4752 | 593448095.6584 | 626747905.5105
Aggregate | Value for Flex-1 | 2289858231.7733 | 67613144.3382 | 92152562.7045 | 117876693.7739 | 144829436.0451 | 173056142.4962 | 202603665.8724 | 233520405.3283 | 234477182.5413 | 235335848.3616 | 212878946.7615 | 230974220.9898 | 297430779.6171 | 323890104.5907 | 348632465.2947 | 374409512.7185 | 401257517.2227 | 429213916.0066 | 458317348.7815 | 488607694.4976 | 520126109.1566 | 552915064.7394 | 587018389.2831 | 622481308.1386 | 659350486.4435 | 697674072.8461 | 737501744.5148 | 778884753.4714
Residential (N-1) | Value for Flex-2 | 20993140.6704 | 1821819.6755 | 1874226.7329 | 1924426.2997 | 1976055.55 | 2029254.3823 | 2084443.2126 | 2141125.9697 | 2191563.8077 | 2243188.231 | 2296023.5477 | 2358750.8421 | 2423330.2384 | 2489831.1903 | 2558030.613 | 2628216.3184 | 2700428.1162 | 2774763.4442 | 2850493.569 | 2928305.2142 | 3008223.5776 | 3090351.7816 | 3173531.4479 | 3258795.4504 | 3346136.4511 | 3435642.5475 | 3525815.175 | 3617882.3431
Commerical(N-1) | Value for Flex-2 | 94629771.5721 | 8212129.0209 | 8448361.7955 | 8674643.9708 | 8907370.6618 | 9147172.4825 | 9395944.5212 | 9651450.6622 | 9878806.8808 | 10111511.8135 | 10349675.0323 | 10632427.8432 | 10923529.2854 | 11223292.431 | 11530711.6922 | 11847084.4241 | 12172590.0756 | 12507667.8621 | 12849032.9071 | 13199780.7218 | 13560024.8889 | 13930230.2481 | 14305175.2334 | 14689515.6809 | 15083218.5136 | 15486680.8437 | 15893147.6646 | 16308154.4145
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 115622912.2425 | 10033948.6964 | 10322588.5284 | 10599070.2705 | 10883426.2117 | 11176426.8648 | 11480387.7338 | 11792576.6319 | 12070370.6885 | 12354700.0445 | 12645698.5801 | 12991178.6852 | 13346859.5239 | 13713123.6212 | 14088742.3052 | 14475300.7425 | 14873018.1918 | 15282431.3062 | 15699526.4761 | 16128085.9359 | 16568248.4665 | 17020582.0297 | 17478706.6813 | 17948311.1313 | 18429354.9647 | 18922323.3912 | 19418962.8397 | 19926036.7575
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 149022625.4435 | 10482482.5597 | 11411304.0271 | 12010929.3859 | 12686212.8587 | 13366594.6033 | 14080244.4665 | 14863848.8842 | 14963452.166 | 15038732.6731 | 15135119.0474 | 15992648.5621 | 16889642.7052 | 17982029.3488 | 19051737.8158 | 20199673.4708 | 21070062.4047 | 22181396.0274 | 23445285.2679 | 24662936.5537 | 25936946.2772 | 27169100.0172 | 28484451.9716 | 29915117.2852 | 31232592.348 | 32586229.6493 | 33751171.1311 | 34819286.064
Aggregate ($M) |  | 2673.0526 | 89200210.9146 | 116584379.5646 | 144448757.27 | 173719898.4703 | 204301417.3549 | 234835499.3264 | 269321634.6078 | 269294422.9247 | 269271424.6389 | 248342513.156 | 267565990.6336 | 338454218.2294 | 369480948.6678 | 397438233.3491 | 425407655.6369 | 456421292.163 | 489667281.8636 | 521828187.0279 | 558040814.7683 | 595053854.0354 | 638852794.9703 | 681385593.2747 | 726367530.2362 | 773725598.0744 | 825360866.8454 | 875579672.9897 | 930643559.3631
Aggregate ($M)+ Monetized Losses |  | 2673.8236 | 89248758.9146 | 116635024.7357 | 144501574.1283 | 173774963.947 | 204358810.8703 | 234895302.8666 | 269390373.2496 | 269363632.2326 | 269367149.8684 | 248465858.2601 | 267689579.8423 | 338578135.0051 | 369605132.1457 | 397562619.4162 | 425532176.808 | 456545877.4521 | 489791856.6508 | 521952672.9222 | 558165129.4659 | 595177911.1729 | 638976503.9729 | 681508859.1999 | 726490253.6121 | 773847674.7322 | 825482187.7471 | 875700124.0498 | 930763021.2637
Project Cost |  | 290
Benefit-Cost Ratio |  | 9.2174

## SCE Orange County
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| SCE Orange County | Losses (MWh) | 43189.3 | 43589.8981 | 43990.4962 | 44391.0942 | 44791.6923 | 45192.2904 | 45592.8885 | 44938.1583 | 44727.1833 | 44510.2417 | 44855.4 | 45186.7083 | 45518.0167 | 45849.325 | 46180.6333 | 46511.9417 | 46843.25 | 47174.5583 | 47505.8667 | 47837.175 | 48168.4833 | 48499.7917 | 48831.1 | 49162.4083 | 49493.7167 | 49825.025 | 50156.3333
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 12.5 | 10 | 10 | 12.5 | 15 | 18.32 | 21.64 | 24.96 | 28.28 | 31.6 | 44.22 | 56.84 | 69.46 | 82.08 | 94.7 | 107.58 | 120.46 | 133.34 | 146.22 | 159.1
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.98 | 5.46 | 6.94 | 8.42 | 9.9 | 11.12 | 12.34 | 13.56 | 14.78 | 16
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0.057282 | 0.057282 | 0.03666 | 0.03666 | 0.057282 | 0.082486 | 0.11556 | 0.14863 | 0.1817 | 0.21477 | 0.24784 | 0.45864 | 0.66943 | 0.88023 | 1.091 | 1.3018 | 1.478 | 1.6543 | 1.8305 | 2.0067 | 2.183
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0.011456 | 0.011456 | 0.0091651 | 0.0091651 | 0.011456 | 0.013748 | 0.017732 | 0.021717 | 0.025702 | 0.029687 | 0.033671 | 0.048152 | 0.062633 | 0.077114 | 0.091594 | 0.10608 | 0.12147 | 0.13686 | 0.15225 | 0.16764 | 0.18304
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 4 | 4 | 5 | 6 | 6.8 | 7.6 | 8.4 | 9.2 | 10 | 12.2 | 14.4 | 16.6 | 18.8 | 21 | 21.4 | 21.8 | 22.2 | 22.6 | 23
N-1 |  | Deficit Flex-1 | 834.5846 | 1109.744 | 1384.9033 | 1660.0627 | 1935.222 | 2210.3814 | 2485.5407 | 2371.5213 | 2257.502 | 2143.4826 | 2200.4923 | 2503.4591 | 2655.175 | 2806.8908 | 2958.6067 | 3110.3225 | 3262.0384 | 3413.7543 | 3565.4701 | 3717.186 | 3868.9019 | 4020.6177 | 4172.3336 | 4324.0494 | 4475.7653 | 4627.4812 | 4779.197
N-1 |  | Deficit Flex-2-1 | 54764.869 | 56456.728 | 57264.1552 | 58102.8917 | 58993.7479 | 60020.7328 | 61060.1837 | 60373.8522 | 59693.002 | 59016.7728 | 60101.9009 | 61230.7643 | 62395.7768 | 63550.1239 | 64740.9783 | 65959.721 | 67215.1918 | 68368.0039 | 69537.8398 | 70717.1799 | 71915.2268 | 72923.2284 | 73911.1796 | 74873.642 | 75812.6644 | 76484.7077 | 77087.5564
N-1 |  | Deficit Flex-2-2 | 9568.3085 | 10808.9102 | 11423.6154 | 12072.2134 | 12781.3992 | 13642.3758 | 14526.5647 | 13941.3055 | 13365.2683 | 12800.1673 | 13710.8124 | 14672.574 | 15689.9995 | 16750.9598 | 17892.045 | 19093.9906 | 20376.8647 | 21588.1705 | 22839.0785 | 24140.8437 | 25479.4572 | 26623.7123 | 27784.108 | 28935.9427 | 30073.1867 | 30898.1375 | 31641.6122
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | [6 empty] | 1964.1807 | 1964.1807 | 1650.8939 | 1650.8939 | 1964.1807 | 2666.7483 | 3399.6862 | 4132.6242 | 4865.5621 | 5598.5001 | 6331.438 | 9280.2368 | 12229.0355 | 15177.8342 | 18126.6329 | 21075.4316 | 25185.7645 | 29296.0974 | 33406.4303 | 37516.7631 | 41627.096
N-1 Monetized | Commercial | $ | [6 empty] | 8150.3401 | 8150.3401 | 6850.3609 | 6850.3609 | 8150.3401 | 11065.6341 | 14106.9498 | 17148.2655 | 20189.5811 | 23230.8968 | 26272.2125 | 38508.211 | 50744.2094 | 62980.2079 | 75216.2064 | 87452.2049 | 104507.973 | 121563.741 | 138619.509 | 155675.277 | 172731.0451
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 2988703.8501 | 3474440.6308 | 3751659.8077 | 4070289.5446 | 4412480.3474 | 4791429.0159 | 5212100.6489 | 5151572.0646 | 5053507.7102 | 5000974.6636 | 5452956.9141 | 5965451.7854 | 6461432.9322 | 7063482.2577 | 7750586.2939 | 8415969.5152 | 9192026.1164 | 9931658.3902 | 10647594.4523 | 11557122.9788 | 12509355.4941 | 13244618.3789 | 14093027.1709 | 14984664.7024 | 15942220.207 | 16719868.7303 | 17575673.8949
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 64341.8678 | Losses (MWh) | 6477.7 | 6513.8923 | 6550.0846 | 6586.2769 | 6622.4692 | 6658.6615 | 6694.8538 | 6760.0263 | 7261.1705 | 7768.2814 | 7713.2923 | 7672.1532 | 7631.0141 | 7589.875 | 7548.7359 | 7507.5968 | 7466.4577 | 7425.3186 | 7384.1795 | 7343.0404 | 7301.9013 | 7260.7622 | 7219.6231 | 7178.484 | 7137.3449 | 7096.2058 | 7055.0667
| 3188562.7007 | Losses ($) | 259108 | 267069.5846 | 275267.306 | 283707.9949 | 292398.6762 | 301346.5741 | 310559.1177 | 321421.8774 | 353881.2477 | 388060.7597 | 394946.6507 | 402661.1943 | 410514.6234 | 418509.0607 | 426646.6482 | 434929.5469 | 443359.9364 | 451940.0144 | 460671.9964 | 469558.115 | 478600.6194 | 487801.7753 | 497163.8636 | 506689.1802 | 516380.0352 | 526238.7523 | 536267.6676
N-1 | 838.7877 | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 54.9 | 45.1 | 39.8 | 31.5 | 41.2 | 60.0667 | 78.1133 | 96.16 | 114.2067 | 132.2533 | 150.3 | 200.01 | 249.72 | 299.43 | 349.14 | 359 | 416.42 | 473.84 | 531.26 | 588.68 | 646.1
N-1 | 79.804 | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 8.9 | 7.7 | 6.1 | 4.3 | 7.1 | 8.8333 | 10.5667 | 12.3 | 14.0333 | 15.7667 | 17.5 | 17.88 | 18.26 | 18.64 | 19.02 | 19.4 | 19.36 | 19.32 | 19.28 | 19.24 | 19.2
N-1 | 71.5256 | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.6737 | 0.56037 | 0.49292 | 0.44519 | 0.50953 | 0.88732 | 1.2572 | 1.6272 | 1.9971 | 2.367 | 2.7369 | 20.6119 | 38.4868 | 56.3618 | 74.2367 | 92.1117 | 79.5842 | 67.0567 | 54.5292 | 42.0016 | 29.4741
N-1 | 1.2897 | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.042691 | 0.034261 | 0.029827 | 0.022628 | 0.030756 | 0.046019 | 0.059588 | 0.073157 | 0.086726 | 0.10029 | 0.11386 | 0.35236 | 0.59085 | 0.82935 | 1.0678 | 1.3063 | 1.1496 | 0.99277 | 0.83599 | 0.67921 | 0.52243
N-1 | 271.7551 | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 27 | 25 | 25 | 25 | 24 | 26.6667 | 29.5333 | 32.4 | 35.2667 | 38.1333 | 41 | 44.4 | 47.8 | 51.2 | 54.6 | 58 | 60.6 | 63.2 | 65.8 | 68.4 | 71
N-1 | 113296.0689 | Flex-1 | 4611.2411 | 6131.5496 | 7651.8581 | 9172.1667 | 10692.4752 | 12212.7837 | 13733.0922 | 13248.6223 | 12764.1524 | 11381.9485 | 12222.6728 | 14409.7739 | 15176.1943 | 15942.6147 | 16709.0351 | 17475.4556 | 18241.876 | 19008.2964 | 19774.7168 | 20541.1373 | 21307.5577 | 22073.9781 | 22840.3985 | 23606.819 | 24373.2394 | 25139.6598 | 25906.0802
N-1 | 1296335.2715 | Flex-2-1 | 138099.7972 | 138782.5139 | 139102.6102 | 139422.4839 | 139750.1759 | 140120.2056 | 140477.5266 | 140243.0428 | 140003.1473 | 139758.4605 | 140148.434 | 140535.4012 | 140930.186 | 141306.8363 | 141680.21 | 142053.9841 | 142428.1801 | 142757.2864 | 143076.0148 | 143384.7278 | 143684.2772 | 143925.9198 | 144158.1313 | 144375.1027 | 144583.1354 | 144729.7599 | 144858.4976
N-1 | 557015.6362 | Flex-2-2 | 48245.8553 | 51382.8367 | 52937.4898 | 54556.2876 | 56286.8275 | 58276.5852 | 60294.1145 | 58957.9768 | 57641.0843 | 56331.4489 | 58432.9525 | 60629.3519 | 62939.628 | 65200.0978 | 67491.3796 | 69851.9805 | 72300.0312 | 74557.5594 | 76861.7796 | 79199.3661 | 81586.0609 | 83613.9316 | 85571.563 | 87458.8558 | 89320.7593 | 90654.6576 | 91859.7549
N-0 | 3662.4319 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 | 603.3371 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 | 54.0898 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 | 2.9079 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 | 81.9765 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 318366.0804 | 1354.9655 | 3468.8297 | 5582.694 | 7696.5582 | 9810.4224 | 11924.2866 | 12073.9701 | 10122.9645 | 8810.6938 | 6959.629 | 10568.2722 | 16552.0592 | 22505.4758 | 28458.8924 | 34412.3089 | 40365.7255 | 46319.1421 | 72017.1463 | 97715.1506 | 123413.1549 | 149111.1591 | 174809.1634 | 216970.3082 | 259131.453 | 301292.5978 | 343453.7426 | 385614.8874
Commerical(N-1) | EENS | 1321055.539 | 5622.4102 | 14393.8598 | 23165.3095 | 31936.7591 | 40708.2087 | 49479.6583 | 50100.7678 | 42005.0976 | 36559.8491 | 28878.882 | 43852.8957 | 68682.5351 | 93386.1528 | 118089.7706 | 142793.3883 | 167497.006 | 192200.6237 | 298834.1282 | 405467.6327 | 512101.1372 | 618734.6417 | 725368.1462 | 900315.2191 | 1075262.292 | 1250209.3649 | 1425156.4378 | 1600103.5107
Aggregate | EENS | 1639421.6194 | 6977.3757 | 17862.6896 | 28748.0034 | 39633.3173 | 50518.6311 | 61403.9449 | 62174.7379 | 52128.0621 | 45370.5429 | 35838.511 | 54421.1679 | 85234.5943 | 115891.6286 | 146548.6629 | 177205.6972 | 207862.7315 | 238519.7658 | 370851.2745 | 503182.7833 | 635514.2921 | 767845.8008 | 900177.3096 | 1117285.5273 | 1334393.745 | 1551501.9627 | 1768610.1804 | 1985718.3981
Residential (N-0) | EENS | 24322736.8672 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21673528.3995
Commerical(N-0) | EENS | 111616614.0139 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98364469.7349
Aggregate | EENS | 135939350.8811 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 120037998.1344
Residential (N-1) | Value for Flex-1 | 604071521.6708 | 18647829 | 25415845.5142 | 32510607.9609 | 39944223.6266 | 47729200.9455 | 55878461.9906 | 64405355.3374 | 63686624.1039 | 62891702.9617 | 57483321.7358 | 63272543.0406 | 76459267.9521 | 82539097.0417 | 88875130.5433 | 95476378.7844 | 102352142.4809 | 109512021.6254 | 116965924.6382 | 124724077.7881 | 132797034.8926 | 141195687.3036 | 149931274.1885 | 159015393.113 | 168460010.9373 | 178277475.0322 | 188480524.825 | 199082303.6856
Commerical(N-1) | Value for Flex-1 | 2488552681.7462 | 76822202.673 | 104703943.5633 | 133931757.6214 | 164555522.4177 | 196626768.1053 | 230198728.8758 | 265326395.9547 | 262365487.396 | 259090704.4119 | 236810161.263 | 260659625.5837 | 314984086.2889 | 340030747.8889 | 366132877.5149 | 393327594.4049 | 421653214.0908 | 451149285.0146 | 481856626.2257 | 513817366.1943 | 547074982.7699 | 581674344.3204 | 617661752.0842 | 655084983.771 | 693993338.4471 | 734437682.7421 | 776470498.4154 | 820145931.3206
Aggregate | Value for Flex-1 | 3092624203.417 | 95470031.6731 | 130119789.0775 | 166442365.5824 | 204499746.0443 | 244355969.0508 | 286077190.8664 | 329731751.2921 | 326052111.4999 | 321982407.3735 | 294293482.9987 | 323932168.6243 | 391443354.2411 | 422569844.9306 | 455008008.0583 | 488803973.1892 | 524005356.5717 | 560661306.64 | 598822550.8639 | 638541443.9824 | 679872017.6625 | 722870031.6241 | 767593026.2727 | 814100376.884 | 862453349.3845 | 912715157.7744 | 964951023.2404 | 1019228235.0062
Residential (N-1) | Value for Flex-2 | 54484024.9767 | 4713071.2638 | 4854780.3021 | 4987627.0978 | 5124073.8167 | 5264520.128 | 5410420.9806 | 5559823.5636 | 5689306.7367 | 5821564.1511 | 5956674.406 | 6122627.9367 | 6293021.6038 | 6468467.1266 | 6647898.6346 | 6832100.9198 | 7021378.1754 | 7215870.6088 | 7413357.7951 | 7615657.0342 | 7822891.4532 | 8035215.3542 | 8249946.8842 | 8469838.8669 | 8694651.4302 | 8924859.2018 | 9157257.822 | 9394538.3207
Commerical(N-1) | Value for Flex-2 | 245595021.67 | 21244884.8934 | 21883659.917 | 22482487.0354 | 23097541.3543 | 23730624.4442 | 24388294.7072 | 25061749.5528 | 25645414.6309 | 26241585.0236 | 26850615.0277 | 27598675.785 | 28366751.1314 | 29157598.485 | 29966413.2729 | 30796733.0638 | 31649929.0548 | 32526633.2525 | 33416836.7537 | 34328731.3144 | 35262871.9483 | 36219954.1955 | 37187889.1965 | 38179085.7219 | 39192462.5121 | 40230159.0236 | 41277731.1184 | 42347309.0222
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 300079046.6467 | 25957956.1572 | 26738440.2191 | 27470114.1332 | 28221615.171 | 28995144.5722 | 29798715.6878 | 30621573.1164 | 31334721.3676 | 32063149.1747 | 32807289.4337 | 33721303.7217 | 34659772.7351 | 35626065.6116 | 36614311.9075 | 37628833.9836 | 38671307.2302 | 39742503.8613 | 40830194.5488 | 41944388.3487 | 43085763.4015 | 44255169.5497 | 45437836.0807 | 46648924.5888 | 47887113.9423 | 49155018.2253 | 50434988.9404 | 51741847.3429
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 186936510.0182 | 13083814.1761 | 14219344.0059 | 14989870.1923 | 15842507.472 | 16648782.24 | 17640263.1073 | 18654978.2169 | 18748867.5797 | 18820379.8744 | 18852678.0327 | 20014983.4449 | 21204176.9907 | 22528950.963 | 23861911.6775 | 25272696.2345 | 26574520.4423 | 27960286.6785 | 29488152.9827 | 31125883.0988 | 32747231.7329 | 34327769.9777 | 36098024.9603 | 37978045.0865 | 39625397.6007 | 41319642.1169 | 42916302.2845 | 44367477.438
Aggregate ($M) |  | 3717.2185 | 135582437.3267 | 173775497.6071 | 212864413.7476 | 253884692.0422 | 296702149.2537 | 340187370.9153 | 388181420.823 | 383948166.3292 | 379439739.7126 | 353669636.1453 | 385295861.1056 | 458133149.6968 | 494678751.9954 | 531227008.9963 | 568694264.6849 | 610524424.6846 | 654775453.1322 | 699374555.2287 | 748692600.3896 | 799114550.8288 | 854248599.0817 | 911975098.0881 | 972356930.0757 | 1036063982.3297 | 1102046626.4293 | 1168982936.8617 | 1237361276.3197
Aggregate ($M)+ Monetized Losses |  | 3720.4071 | 135841545.3267 | 174042567.1917 | 213139681.0535 | 254168400.0371 | 296994547.9299 | 340488717.4893 | 388491979.9407 | 384269588.2067 | 379793620.9603 | 354057696.905 | 385690807.7563 | 458535810.8911 | 495089266.6187 | 531645518.0569 | 569120911.333 | 610959354.2315 | 655218813.0686 | 699826495.2432 | 749153272.386 | 799584108.9437 | 854727199.7012 | 912462899.8634 | 972854093.9394 | 1036570671.5099 | 1102563006.4645 | 1169509175.614 | 1237897543.9873
Project Cost |  | 806
Benefit-Cost Ratio |  | 4.6159

## VS to VN & Central BESS VS VN
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Energy Storage at Pechanga and Allesando + Ties between VN+VS | Losses (MWh) | 49328.2 | 49736.2913 | 50144.3827 | 50552.474 | 50960.5654 | 51368.6567 | 51776.7481 | 51089 | 50877.45 | 50664.2 | 51004.825 | 51341.9516 | 51679.0781 | 52016.2047 | 52353.3312 | 52690.4578 | 53027.5844 | 53364.7109 | 53701.8375 | 54038.9641 | 54376.0906 | 54713.2172 | 55050.3437 | 55387.4703 | 55724.5969 | 56061.7234 | 56398.85
N-1 |  | EENS | 5.8 | 14.4833 | 23.1667 | 31.85 | 40.5333 | 49.2167 | 57.9 | 52.5 | 44.1 | 35.9 | 48.5 | 61.1 | 82.38 | 103.66 | 124.94 | 146.22 | 167.5 | 220.02 | 272.54 | 325.06 | 377.58 | 430.1 | 490.7 | 551.3 | 611.9 | 672.5 | 733.1
N-1 |  | IP | 3 | 4.9167 | 6.8333 | 8.75 | 10.6667 | 12.5833 | 14.5 | 13.5 | 11.8 | 10.1 | 12.9 | 15.1 | 17.26 | 19.42 | 21.58 | 23.74 | 25.9 | 27.82 | 29.74 | 31.66 | 33.58 | 35.5 | 36.58 | 37.66 | 38.74 | 39.82 | 40.9
N-1 |  | SAIDI | 0.015894 | 0.083764 | 0.15163 | 0.2195 | 0.28737 | 0.35524 | 0.42311 | 0.33569 | 0.28198 | 0.19676 | 0.31012 | 0.4465 | 0.87624 | 1.306 | 1.7357 | 2.1655 | 2.5952 | 4.3788 | 6.1623 | 7.9458 | 9.7293 | 11.5128 | 14.8115 | 18.1102 | 21.4089 | 24.7076 | 28.0063
N-1 |  | SAIFI | 0.005298 | 0.01323 | 0.021162 | 0.029094 | 0.037025 | 0.044957 | 0.052889 | 0.047956 | 0.040283 | 0.032793 | 0.044303 | 0.055812 | 0.075253 | 0.094694 | 0.11414 | 0.13358 | 0.15302 | 0.20155 | 0.25009 | 0.29862 | 0.34715 | 0.39569 | 0.45221 | 0.50874 | 0.56527 | 0.62179 | 0.67832
N-1 |  | PFD | 3 | 3.8333 | 4.6667 | 5.5 | 6.3333 | 7.1667 | 8 | 7 | 7 | 6 | 7 | 8 | 9.8 | 11.6 | 13.4 | 15.2 | 17 | 19.6 | 22.2 | 24.8 | 27.4 | 30 | 32.8 | 35.6 | 38.4 | 41.2 | 44
N-1 |  | Deficit Flex-1 | 3808.3607 | 5063.9626 | 6319.5645 | 7575.1665 | 8830.7684 | 10086.3703 | 11341.9723 | 10868.4556 | 10394.9389 | 9921.4223 | 10158.1806 | 11732.4477 | 12452.8192 | 13173.1908 | 13893.5623 | 14613.9339 | 15334.3054 | 16054.677 | 16775.0485 | 17495.4201 | 18215.7916 | 18936.1632 | 19656.5347 | 20376.9063 | 21097.2778 | 21817.6494 | 22538.0209
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 15863.8465 | 17648.2938 | 18532.2445 | 19475.1482 | 20493.6788 | 21703.1962 | 22945.9872 | 22121.1674 | 21313.2168 | 20520.3431 | 21799.1819 | 23155.1608 | 24606.2129 | 26062.5347 | 27614.3526 | 29256.497 | 30979.0521 | 32583.3718 | 34238.6898 | 35926.361 | 37681.7452 | 39178.6708 | 40662.7614 | 42131.1117 | 43588.0399 | 44646.03 | 45597.0962
|  | EENS(Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS(Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 1269.4985 | 3507.3999 | 5745.3013 | 7983.2026 | 10221.104 | 12459.0054 | 14696.9068 | 13659.3661 | 11760.7142 | 9813.2626 | 13588.9086 | 17547.2036 | 24911.6828 | 32276.162 | 39640.6412 | 47005.1204 | 54369.5996 | 77256.7859 | 100143.9722 | 123031.1586 | 145918.3449 | 168805.5312 | 204593.5776 | 240381.624 | 276169.6704 | 311957.7168 | 347745.7632
N-1 Monetized | Commercial | $ | 5267.7659 | 14553.906 | 23840.0461 | 33126.1863 | 42412.3264 | 51698.4665 | 60984.6067 | 56679.3462 | 48800.9171 | 40719.9943 | 56386.9837 | 72811.8726 | 103370.6747 | 133929.4768 | 164488.2789 | 195047.081 | 225605.8831 | 320575.9384 | 415545.9936 | 510516.0489 | 605486.1042 | 700456.1595 | 848958.1509 | 997460.1423 | 1145962.1336 | 1294464.125 | 1442966.1164
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 4851883.8074 | 5548866.4784 | 5954619.7491 | 6363793.1776 | 6862681.5292 | 7430776.4174 | 7958064.5941 | 7957168.049 | 7874171.1774 | 7776287.7266 | 8450702.8694 | 9080603.7964 | 9916810.716 | 10742147.0818 | 11532452.8263 | 12410650.1702 | 13427370.4397 | 14508754.4423 | 15576671.5917 | 16678510.3769 | 17727086.4233 | 18931202.4562 | 20126360.6731 | 21277070.9728 | 22513024.6587 | 23603677.4869 | 24710377.8006
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 7386.6021 | Losses (MWh) | 338.8 | 367.499 | 396.1981 | 424.8971 | 453.5962 | 482.2952 | 510.9942 | 609.1846 | 1110.9038 | 1614.3231 | 1563.8673 | 1516.91 | 1469.9526 | 1422.9953 | 1376.038 | 1329.0806 | 1282.1233 | 1235.166 | 1188.2087 | 1141.2513 | 1094.294 | 1047.3367 | 1000.3793 | 953.422 | 906.4647 | 859.5073 | 812.55
| 387169.6632 | Losses ($) | 13552 | 15067.4606 | 16650.2242 | 18302.7088 | 20027.4113 | 21826.9097 | 23703.8658 | 28965.1629 | 54141.1386 | 80642.7325 | 80075.2948 | 79612.6936 | 79076.9153 | 78464.5902 | 77772.2257 | 76996.2027 | 76132.7708 | 75178.0448 | 74127.9994 | 72978.4655 | 71725.1249 | 70363.5058 | 68888.9774 | 67296.7455 | 65581.8464 | 63739.1418 | 61763.3134
N-1 | 114.4291 | EENS | 4.2 | 6.0167 | 6.7133 | 7.41 | 8.1067 | 8.8033 | 9.5 | 5.1 | 5.7 | 5.6 | 5.2 | 13.9667 | 14.0533 | 14.14 | 14.2267 | 14.3133 | 14.4 | 24.21 | 34.02 | 43.83 | 53.64 | 23.6 | 33.3 | 43 | 52.7 | 62.4 | 72.1
N-1 | -30.4126 | IP | -1 | -1.9167 | -2.1533 | -2.39 | -2.6267 | -2.8633 | -3.1 | -3.3 | -3.2 | -3.3 | -3.3 | -3.7667 | -4.1933 | -4.62 | -5.0467 | -5.4733 | -5.9 | -5.96 | -6.02 | -6.08 | -6.14 | -6.2 | -6.1 | -6 | -5.9 | -5.8 | -5.7
N-1 | 54.4087 | SAIDI | 0.068918 | 0.15907 | 0.18883 | 0.21859 | 0.24835 | 0.27811 | 0.30787 | 0.28195 | 0.24759 | 0.28509 | 0.25669 | 0.52331 | 0.49656 | 0.4698 | 0.44305 | 0.4163 | 0.38955 | 16.6918 | 32.994 | 49.2962 | 65.5984 | 81.9007 | 66.2507 | 50.6007 | 34.9507 | 19.3008 | 3.6508
N-1 | 0.65104 | SAIFI | 0.00075996 | 0.0045419 | 0.0038851 | 0.0032282 | 0.0025714 | 0.0019146 | 0.0012578 | -0.0022394 | -0.0012916 | -0.0010002 | -0.00209 | 0.0039543 | 0.002067 | 0.00017976 | -0.0017075 | -0.0035948 | -0.005482 | 0.19896 | 0.4034 | 0.60784 | 0.81228 | 1.0167 | 0.81881 | 0.62089 | 0.42298 | 0.22506 | 0.027145
N-1 | 225.5303 | PFD | 11 | 17.1667 | 18.5333 | 19.9 | 21.2667 | 22.6333 | 24 | 23 | 22 | 23 | 22 | 24.6667 | 26.5333 | 28.4 | 30.2667 | 32.1333 | 34 | 37 | 40 | 43 | 46 | 49 | 49.2 | 49.4 | 49.6 | 49.8 | 50
N-1 | 39141.4455 | Flex-1 | 1637.465 | 2177.331 | 2717.1969 | 3257.0628 | 3796.9288 | 4336.7947 | 4876.6607 | 4751.6881 | 4626.7154 | 3604.0089 | 4264.9845 | 5180.7853 | 5378.55 | 5576.3147 | 5774.0795 | 5971.8442 | 6169.609 | 6367.3737 | 6565.1384 | 6762.9032 | 6960.6679 | 7158.4327 | 7356.1974 | 7553.9621 | 7751.7269 | 7949.4916 | 8147.2564
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 479183.4057 | Flex-2-2 | 41950.3173 | 44543.4531 | 45828.8607 | 47153.3528 | 48574.548 | 50215.7648 | 51874.692 | 50778.1149 | 49693.1357 | 48611.2731 | 50344.583 | 52146.7651 | 54023.4147 | 55888.5229 | 57769.072 | 59689.4741 | 61697.8438 | 63562.3581 | 65462.1684 | 67413.8488 | 69383.773 | 71058.9731 | 72692.9097 | 74263.6867 | 75805.9061 | 76906.7651 | 77904.2708
N-0 | 3662.4319 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 | 603.3371 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 | 54.0898 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 | 2.9079 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 | 81.9765 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 34143.207 | 85.4671 | -38.5701 | -162.6073 | -286.6445 | -410.6816 | -534.7188 | -658.756 | -1572.2209 | -1299.1265 | -1202.7397 | -1056.4557 | 1671.6039 | 993.4792 | 315.3545 | -362.7701 | -1040.8948 | -1719.0195 | 4040.5972 | 9800.2139 | 15559.8305 | 21319.4472 | 27079.0638 | 37562.4951 | 48045.9264 | 58529.3577 | 69012.789 | 79496.2203
Commerical(N-1) | EENS | 141676.7537 | 354.6443 | -160.0462 | -674.7367 | -1189.4272 | -1704.1177 | -2218.8082 | -2733.4987 | -6523.9084 | -5390.7071 | -4990.7514 | -4383.7478 | 6936.2967 | 4122.428 | 1308.5592 | -1505.3095 | -4319.1782 | -7133.0469 | 16766.4008 | 40665.8485 | 64565.2962 | 88464.7439 | 112364.1916 | 155865.0412 | 199365.8907 | 242866.7403 | 286367.5899 | 329868.4394
Aggregate | EENS | 175819.9607 | 440.1114 | -198.6163 | -837.344 | -1476.0717 | -2114.7993 | -2753.527 | -3392.2547 | -8096.1293 | -6689.8336 | -6193.4911 | -5440.2035 | 8607.9006 | 5115.9072 | 1623.9138 | -1868.0796 | -5360.073 | -8852.0664 | 20806.998 | 50466.0623 | 80125.1267 | 109784.1911 | 139443.2555 | 193427.5363 | 247411.8171 | 301396.098 | 355380.3788 | 409364.6597
Residential (N-0) | EENS | 24322736.8672 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21673528.3995
Commerical(N-0) | EENS | 111616614.0139 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98364469.7349
Aggregate | EENS | 135939350.8811 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 120037998.1344
Residential (N-1) | Value for Flex-1 | 207361752.6799 | 6621897.889 | 9025240.0833 | 11544610.7011 | 14184309.0748 | 16948776.9855 | 19842603.0985 | 22870527.5316 | 22841542.6096 | 22796814.3618 | 18201663.851 | 22078347.207 | 27489608.933 | 29252436.5342 | 31086224.5099 | 32993419.1115 | 34976544.5529 | 37038205.3794 | 39181088.9069 | 41407967.7324 | 43721702.3186 | 46125243.6543 | 48621635.9928 | 51214019.671 | 53905634.0105 | 56699820.3048 | 59600024.8925 | 62609802.3219
Commerical(N-1) | Value for Flex-1 | 854254218.5995 | 27279785.8511 | 37180672.4982 | 47559553.6114 | 58434140.8601 | 69822732.7501 | 81744232.8966 | 94218168.8424 | 94098761.6153 | 93914497.6713 | 74984166.2182 | 90954677.0199 | 113247086.7709 | 120509288.6742 | 128063821.2434 | 135920762.1357 | 144090510.1843 | 152583795.159 | 161411687.8136 | 170585610.2289 | 180117346.4601 | 190019053.4965 | 200303272.5432 | 210982940.6337 | 222071402.5835 | 233582423.2928 | 245530200.411 | 257929377.3705
Aggregate | Value for Flex-1 | 1061615971.2793 | 33901683.7401 | 46205912.5815 | 59104164.3126 | 72618449.9349 | 86771509.7356 | 101586835.9951 | 117088696.374 | 116940304.2249 | 116711312.0331 | 93185830.0692 | 113033024.2269 | 140736695.704 | 149761725.2085 | 159150045.7534 | 168914181.2472 | 179067054.7372 | 189622000.5384 | 200592776.7205 | 211993577.9613 | 223839048.7787 | 236144297.1508 | 248924908.536 | 262196960.3047 | 275977036.594 | 290282243.5976 | 305130225.3035 | 320539179.6924
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 158850774.4516 | 11220634.2188 | 12144918.1584 | 12786910.2509 | 13549003.8391 | 14198581.0583 | 15000915.7058 | 15909014.2717 | 15943271.5953 | 15999716.4072 | 16077364.9697 | 17017237.4897 | 18089024.9798 | 19073573.1791 | 20183246.8534 | 21490829.7021 | 22579839.7873 | 23724942.3552 | 24911056.9306 | 26196805.9595 | 27625844.3348 | 29110039.0485 | 30411440.883 | 31944711.5843 | 33332991.3303 | 34748837.6652 | 36032493.5279 | 37232773.5323
Aggregate ($M) |  | 1356.5819 | 46186416.015 | 61030693.7386 | 75823553.0558 | 91447167.7399 | 107619710.7541 | 123194795.4827 | 142105261.8508 | 140635817.5108 | 139232771.3537 | 116937348.717 | 137617805.6599 | 169574939.7199 | 182678413.1563 | 194931145.2106 | 207214698.4501 | 222706912.1605 | 239510927.0138 | 255387446.2078 | 274818552.1596 | 294319041.9801 | 317391902.5198 | 341421826.1392 | 366847397.4144 | 394321167.3987 | 422637783.7108 | 450430111.4262 | 478219316.0189
Aggregate ($M)+ Monetized Losses |  | 1356.9691 | 46199968.015 | 61045761.1992 | 75840203.28 | 91465470.4487 | 107639738.1653 | 123216622.3923 | 142128965.7166 | 140664782.6737 | 139286912.4923 | 117017991.4495 | 137697880.9547 | 169654552.4135 | 182757490.0717 | 195009609.8008 | 207292470.6758 | 222783908.3632 | 239587059.7847 | 255462624.2526 | 274892680.159 | 294392020.4456 | 317463627.6447 | 341492189.645 | 366916286.3919 | 394388464.1442 | 422703365.5571 | 450493850.568 | 478281079.3323
Project Cost |  | 239
Benefit-Cost Ratio |  | 5.6777
Market Participation Revenue (All costs are $x1,000) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3528.0526 | 4041.8256 | 4555.5986 | 5069.3717 | 5583.1447 | 6096.9177 | 6165.2503 | 6233.5829 | 6301.9156

## VS to VN to VST & Cen BESS VS
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Valley South to Valley North to Vista and Centralized BESS in Valley South | Losses (MWh) | 49328.2 | 49736.2913 | 50144.3827 | 50552.474 | 50960.5654 | 51368.6567 | 51776.7481 | 51089 | 50877.45 | 50664.2 | 51004.825 | 51341.9516 | 51679.0781 | 52016.2047 | 52353.3312 | 52690.4578 | 53027.5844 | 53364.7109 | 53701.8375 | 54038.9641 | 54376.0906 | 54713.2172 | 55050.3437 | 55387.4703 | 55724.5969 | 56061.7234 | 56398.85
N-1 |  | EENS | 5.8 | 14.4833 | 23.1667 | 31.85 | 40.5333 | 49.2167 | 57.9 | 52.5 | 44.1 | 35.9 | 48.5 | 61.1 | 82.38 | 103.66 | 124.94 | 146.22 | 167.5 | 220.02 | 272.54 | 325.06 | 377.58 | 430.1 | 490.7 | 551.3 | 611.9 | 672.5 | 733.1
N-1 |  | IP | 3 | 4.9167 | 6.8333 | 8.75 | 10.6667 | 12.5833 | 14.5 | 13.5 | 11.8 | 10.1 | 12.9 | 15.1 | 17.26 | 19.42 | 21.58 | 23.74 | 25.9 | 27.82 | 29.74 | 31.66 | 33.58 | 35.5 | 36.58 | 37.66 | 38.74 | 39.82 | 40.9
N-1 |  | SAIDI | 0.015894 | 0.083764 | 0.15163 | 0.2195 | 0.28737 | 0.35524 | 0.42311 | 0.33569 | 0.28198 | 0.19676 | 0.31012 | 0.4465 | 0.87624 | 1.306 | 1.7357 | 2.1655 | 2.5952 | 4.3788 | 6.1623 | 7.9458 | 9.7293 | 11.5128 | 14.8115 | 18.1102 | 21.4089 | 24.7076 | 28.0063
N-1 |  | SAIFI | 0.005298 | 0.01323 | 0.021162 | 0.029094 | 0.037025 | 0.044957 | 0.052889 | 0.047956 | 0.040283 | 0.032793 | 0.044303 | 0.055812 | 0.075253 | 0.094694 | 0.11414 | 0.13358 | 0.15302 | 0.20155 | 0.25009 | 0.29862 | 0.34715 | 0.39569 | 0.45221 | 0.50874 | 0.56527 | 0.62179 | 0.67832
N-1 |  | PFD | 3 | 3.8333 | 4.6667 | 5.5 | 6.3333 | 7.1667 | 8 | 7 | 7 | 6 | 7 | 8 | 9.8 | 11.6 | 13.4 | 15.2 | 17 | 19.6 | 22.2 | 24.8 | 27.4 | 30 | 32.8 | 35.6 | 38.4 | 41.2 | 44
N-1 |  | Deficit Flex-1 | 3808.3607 | 5063.9626 | 6319.5645 | 7575.1665 | 8830.7684 | 10086.3703 | 11341.9723 | 10868.4556 | 10394.9389 | 9921.4223 | 10158.1806 | 11732.4477 | 12452.8192 | 13173.1908 | 13893.5623 | 14613.9339 | 15334.3054 | 16054.677 | 16775.0485 | 17495.4201 | 18215.7916 | 18936.1632 | 19656.5347 | 20376.9063 | 21097.2778 | 21817.6494 | 22538.0209
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 15863.8465 | 17648.2938 | 18532.2445 | 19475.1482 | 20493.6788 | 21703.1962 | 22945.9872 | 22121.1674 | 21313.2168 | 20520.3431 | 21799.1819 | 23155.1608 | 24606.2129 | 26062.5347 | 27614.3526 | 29256.497 | 30979.0521 | 32583.3718 | 34238.6898 | 35926.361 | 37681.7452 | 39178.6708 | 40662.7614 | 42131.1117 | 43588.0399 | 44646.03 | 45597.0962
N-0 |  | EENS (Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS (Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.2 | 23.4 | 45.6 | 67.8
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 13 | 24.8 | 36.6
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010438 | 0.098983 | 0.19692 | 0.29486
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010438 | 0.020353 | 0.039663 | 0.058972
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.3333 | 3.6667 | 5
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6994.7817 | 167735.6248 | 356801.1495 | 844489.8402
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41845.5858 | 1003461.6962 | 2036605.0335 | 4817272.6303
N-1 Monetized | Residential | $ | 1269.4985 | 3507.3999 | 5745.3013 | 7983.2026 | 10221.104 | 12459.0054 | 14696.9068 | 13659.3661 | 11760.7142 | 9813.2626 | 13588.9086 | 17547.2036 | 24911.6828 | 32276.162 | 39640.6412 | 47005.1204 | 54369.5996 | 77256.7859 | 100143.9722 | 123031.1586 | 145918.3449 | 168805.5312 | 204593.5776 | 240381.624 | 276169.6704 | 311957.7168 | 347745.7632
N-1 Monetized | Commercial | $ | 5267.7659 | 14553.906 | 23840.0461 | 33126.1863 | 42412.3264 | 51698.4665 | 60984.6067 | 56679.3462 | 48800.9171 | 40719.9943 | 56386.9837 | 72811.8726 | 103370.6747 | 133929.4768 | 164488.2789 | 195047.081 | 225605.8831 | 320575.9384 | 415545.9936 | 510516.0489 | 605486.1042 | 700456.1595 | 848958.1509 | 997460.1423 | 1145962.1336 | 1294464.125 | 1442966.1164
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 4851883.8074 | 5548866.4784 | 5954619.7491 | 6363793.1776 | 6862681.5292 | 7430776.4174 | 7958064.5941 | 7957168.049 | 7874171.1774 | 7776287.7266 | 8450702.8694 | 9080603.7964 | 9916810.716 | 10742147.0818 | 11532452.8263 | 12410650.1702 | 13427370.4397 | 14508754.4423 | 15576671.5917 | 16678510.3769 | 17727086.4233 | 18931202.4562 | 20126360.6731 | 21277070.9728 | 22513024.6587 | 23603677.4869 | 24710377.8006
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 7386.6021 | Losses (MWh) | 338.8 | 367.499 | 396.1981 | 424.8971 | 453.5962 | 482.2952 | 510.9942 | 609.1846 | 1110.9038 | 1614.3231 | 1563.8673 | 1516.91 | 1469.9526 | 1422.9953 | 1376.038 | 1329.0806 | 1282.1233 | 1235.166 | 1188.2087 | 1141.2513 | 1094.294 | 1047.3367 | 1000.3793 | 953.422 | 906.4647 | 859.5073 | 812.55
| 387169.6632 | Losses ($) | 13552 | 15067.4606 | 16650.2242 | 18302.7088 | 20027.4113 | 21826.9097 | 23703.8658 | 28965.1629 | 54141.1386 | 80642.7325 | 80075.2948 | 79612.6936 | 79076.9153 | 78464.5902 | 77772.2257 | 76996.2027 | 76132.7708 | 75178.0448 | 74127.9994 | 72978.4655 | 71725.1249 | 70363.5058 | 68888.9774 | 67296.7455 | 65581.8464 | 63739.1418 | 61763.3134
N-1 | 114.4291 | EENS | 4.2 | 6.0167 | 6.7133 | 7.41 | 8.1067 | 8.8033 | 9.5 | 5.1 | 5.7 | 5.6 | 5.2 | 13.9667 | 14.0533 | 14.14 | 14.2267 | 14.3133 | 14.4 | 24.21 | 34.02 | 43.83 | 53.64 | 23.6 | 33.3 | 43 | 52.7 | 62.4 | 72.1
N-1 | -30.4126 | IP | -1 | -1.9167 | -2.1533 | -2.39 | -2.6267 | -2.8633 | -3.1 | -3.3 | -3.2 | -3.3 | -3.3 | -3.7667 | -4.1933 | -4.62 | -5.0467 | -5.4733 | -5.9 | -5.96 | -6.02 | -6.08 | -6.14 | -6.2 | -6.1 | -6 | -5.9 | -5.8 | -5.7
N-1 | 54.4087 | SAIDI | 0.068918 | 0.15907 | 0.18883 | 0.21859 | 0.24835 | 0.27811 | 0.30787 | 0.28195 | 0.24759 | 0.28509 | 0.25669 | 0.52331 | 0.49656 | 0.4698 | 0.44305 | 0.4163 | 0.38955 | 16.6918 | 32.994 | 49.2962 | 65.5984 | 81.9007 | 66.2507 | 50.6007 | 34.9507 | 19.3008 | 3.6508
N-1 | 0.65104 | SAIFI | 0.00075996 | 0.0045419 | 0.0038851 | 0.0032282 | 0.0025714 | 0.0019146 | 0.0012578 | -0.0022394 | -0.0012916 | -0.0010002 | -0.00209 | 0.0039543 | 0.002067 | 0.00017976 | -0.0017075 | -0.0035948 | -0.005482 | 0.19896 | 0.4034 | 0.60784 | 0.81228 | 1.0167 | 0.81881 | 0.62089 | 0.42298 | 0.22506 | 0.027145
N-1 | 225.5303 | PFD | 11 | 17.1667 | 18.5333 | 19.9 | 21.2667 | 22.6333 | 24 | 23 | 22 | 23 | 22 | 24.6667 | 26.5333 | 28.4 | 30.2667 | 32.1333 | 34 | 37 | 40 | 43 | 46 | 49 | 49.2 | 49.4 | 49.6 | 49.8 | 50
N-1 | 39141.4455 | Flex-1 | 1637.465 | 2177.331 | 2717.1969 | 3257.0628 | 3796.9288 | 4336.7947 | 4876.6607 | 4751.6881 | 4626.7154 | 3604.0089 | 4264.9845 | 5180.7853 | 5378.55 | 5576.3147 | 5774.0795 | 5971.8442 | 6169.609 | 6367.3737 | 6565.1384 | 6762.9032 | 6960.6679 | 7158.4327 | 7356.1974 | 7553.9621 | 7751.7269 | 7949.4916 | 8147.2564
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 479183.4057 | Flex-2-2 | 41950.3173 | 44543.4531 | 45828.8607 | 47153.3528 | 48574.548 | 50215.7648 | 51874.692 | 50778.1149 | 49693.1357 | 48611.2731 | 50344.583 | 52146.7651 | 54023.4147 | 55888.5229 | 57769.072 | 59689.4741 | 61697.8438 | 63562.3581 | 65462.1684 | 67413.8488 | 69383.773 | 71058.9731 | 72692.9097 | 74263.6867 | 75805.9061 | 76906.7651 | 77904.2708
N-0 | 3651.1526 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2079.2 | 2250 | 2420.8 | 2591.6
N-0 | 597.1428 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 177.48 | 172.52 | 167.56 | 162.6
N-0 | 54.0416 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6792 | 66.2366 | 83.794 | 101.3514
N-0 | 2.8981 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3307 | 1.7832 | 2.2357 | 2.6882
N-0 | 80.9706 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 31.2 | 31.4667 | 31.7333 | 32
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 34143.207 | 85.4671 | -38.5701 | -162.6073 | -286.6445 | -410.6816 | -534.7188 | -658.756 | -1572.2209 | -1299.1265 | -1202.7397 | -1056.4557 | 1671.6039 | 993.4792 | 315.3545 | -362.7701 | -1040.8948 | -1719.0195 | 4040.5972 | 9800.2139 | 15559.8305 | 21319.4472 | 27079.0638 | 37562.4951 | 48045.9264 | 58529.3577 | 69012.789 | 79496.2203
Commerical(N-1) | EENS | 141676.7537 | 354.6443 | -160.0462 | -674.7367 | -1189.4272 | -1704.1177 | -2218.8082 | -2733.4987 | -6523.9084 | -5390.7071 | -4990.7514 | -4383.7478 | 6936.2967 | 4122.428 | 1308.5592 | -1505.3095 | -4319.1782 | -7133.0469 | 16766.4008 | 40665.8485 | 64565.2962 | 88464.7439 | 112364.1916 | 155865.0412 | 199365.8907 | 242866.7403 | 286367.5899 | 329868.4394
Aggregate | EENS | 175819.9607 | 440.1114 | -198.6163 | -837.344 | -1476.0717 | -2114.7993 | -2753.527 | -3392.2547 | -8096.1293 | -6689.8336 | -6193.4911 | -5440.2035 | 8607.9006 | 5115.9072 | 1623.9138 | -1868.0796 | -5360.073 | -8852.0664 | 20806.998 | 50466.0623 | 80125.1267 | 109784.1911 | 139443.2555 | 193427.5363 | 247411.8171 | 301396.098 | 355380.3788 | 409364.6597
Residential (N-0) | EENS | 24212192.0993 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15543246.7169 | 17584078.6321 | 19396291.004 | 20829038.5593
Commerical(N-0) | EENS | 110981417.4476 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69171640.5729 | 78550030.3969 | 87122315.029 | 93547197.1047
Aggregate | EENS | 135193609.5469 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84714887.2898 | 96134109.029 | 106518606.033 | 114376235.664
Residential (N-1) | Value for Flex-1 | 207361752.6799 | 6621897.889 | 9025240.0833 | 11544610.7011 | 14184309.0748 | 16948776.9855 | 19842603.0985 | 22870527.5316 | 22841542.6096 | 22796814.3618 | 18201663.851 | 22078347.207 | 27489608.933 | 29252436.5342 | 31086224.5099 | 32993419.1115 | 34976544.5529 | 37038205.3794 | 39181088.9069 | 41407967.7324 | 43721702.3186 | 46125243.6543 | 48621635.9928 | 51214019.671 | 53905634.0105 | 56699820.3048 | 59600024.8925 | 62609802.3219
Commerical(N-1) | Value for Flex-1 | 854254218.5995 | 27279785.8511 | 37180672.4982 | 47559553.6114 | 58434140.8601 | 69822732.7501 | 81744232.8966 | 94218168.8424 | 94098761.6153 | 93914497.6713 | 74984166.2182 | 90954677.0199 | 113247086.7709 | 120509288.6742 | 128063821.2434 | 135920762.1357 | 144090510.1843 | 152583795.159 | 161411687.8136 | 170585610.2289 | 180117346.4601 | 190019053.4965 | 200303272.5432 | 210982940.6337 | 222071402.5835 | 233582423.2928 | 245530200.411 | 257929377.3705
Aggregate | Value for Flex-1 | 1061615971.2793 | 33901683.7401 | 46205912.5815 | 59104164.3126 | 72618449.9349 | 86771509.7356 | 101586835.9951 | 117088696.374 | 116940304.2249 | 116711312.0331 | 93185830.0692 | 113033024.2269 | 140736695.704 | 149761725.2085 | 159150045.7534 | 168914181.2472 | 179067054.7372 | 189622000.5384 | 200592776.7205 | 211993577.9613 | 223839048.7787 | 236144297.1508 | 248924908.536 | 262196960.3047 | 275977036.594 | 290282243.5976 | 305130225.3035 | 320539179.6924
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 158850774.4516 | 11220634.2188 | 12144918.1584 | 12786910.2509 | 13549003.8391 | 14198581.0583 | 15000915.7058 | 15909014.2717 | 15943271.5953 | 15999716.4072 | 16077364.9697 | 17017237.4897 | 18089024.9798 | 19073573.1791 | 20183246.8534 | 21490829.7021 | 22579839.7873 | 23724942.3552 | 24911056.9306 | 26196805.9595 | 27625844.3348 | 29110039.0485 | 30411440.883 | 31944711.5843 | 33332991.3303 | 34748837.6652 | 36032493.5279 | 37232773.5323
Aggregate ($M) |  | 1355.8362 | 46186416.015 | 61030693.7386 | 75823553.0558 | 91447167.7399 | 107619710.7541 | 123194795.4827 | 142105261.8508 | 140635817.5108 | 139232771.3537 | 116937348.717 | 137617805.6599 | 169574939.7199 | 182678413.1563 | 194931145.2106 | 207214698.4501 | 222706912.1605 | 239510927.0138 | 255387446.2078 | 274818552.1596 | 294319041.9801 | 317391902.5198 | 341421826.1392 | 366847397.4144 | 394272327.0312 | 421466586.3898 | 448036705.2432 | 472557553.5485
Aggregate ($M)+ Monetized Losses |  | 1356.2233 | 46199968.015 | 61045761.1992 | 75840203.28 | 91465470.4487 | 107639738.1653 | 123216622.3923 | 142128965.7166 | 140664782.6737 | 139286912.4923 | 117017991.4495 | 137697880.9547 | 169654552.4135 | 182757490.0717 | 195009609.8008 | 207292470.6758 | 222783908.3632 | 239587059.7847 | 255462624.2526 | 274892680.159 | 294392020.4456 | 317463627.6447 | 341492189.645 | 366916286.3919 | 394339623.7768 | 421532168.2362 | 448100444.385 | 472619316.8618
Project Cost |  | 270
Benefit-Cost Ratio |  | 5.023
Market Participation Revenue (All costs are $x1,000) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## SDG&E and Central BESS in VS
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| SDG&E and Centralized BESS in Valley South | Losses (MWh) | 44182.4 | 44577.579 | 44972.7581 | 45367.9371 | 45763.1162 | 46158.2952 | 46553.4742 | 45135.34 | 44990.69 | 44840.08 | 45077.67 | 45309.7384 | 45541.8069 | 45773.8753 | 46005.9438 | 46238.0122 | 46470.0806 | 46702.1491 | 46934.2175 | 47166.2859 | 47398.3544 | 47630.4228 | 47862.4913 | 48094.5597 | 48326.6281 | 48558.6966 | 48789.6475
N-1 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 |  | Deficit Flex-1 | 1522.8473 | 1930.4719 | 2338.0965 | 2745.7211 | 3153.3457 | 3560.9703 | 3968.5949 | 4640.9263 | 5313.2576 | 5985.589 | 5649.4233 | 9531.5857 | 10245.3391 | 10959.0925 | 11672.8459 | 12386.5993 | 13100.3528 | 13814.1062 | 14527.8596 | 15241.613 | 15955.3664 | 16669.1199 | 17382.8733 | 18096.6267 | 18810.3801 | 19524.1335 | 19840.4662
N-1 |  | Deficit Flex-2-1 | 57103.9364 | 58857.6368 | 59699.6043 | 60571.995 | 61496.8629 | 62558.6521 | 63631.2349 | 62922.9382 | 62220.1254 | 61520.6663 | 62642.0385 | 63807.6263 | 65017.0585 | 66209.8025 | 67437.5589 | 68700.8853 | 70007.3228 | 71205.5074 | 72422.1093 | 73645.384 | 74886.792 | 75927.3849 | 76947.7251 | 77938.9668 | 78904.9135 | 79596.3231 | 80217.6368
N-1 |  | Deficit Flex-2-2 | 12005.7424 | 13453.7958 | 14178.8955 | 14937.2899 | 15757.2593 | 16749.9297 | 17791.8608 | 17102.1785 | 16427.9266 | 15778.9354 | 16830.1823 | 17964.2326 | 19172.9939 | 20408.244 | 21719.8418 | 23098.2324 | 24567.0678 | 25931.8136 | 27355.4567 | 28834.2072 | 30356.2803 | 31653.1061 | 32946.7014 | 34221.3621 | 35477.9187 | 36390.7641 | 37223.1347
N-0 |  | EENS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 3761250.6801 | 4284487.0478 | 4606811.8682 | 4995927.6228 | 5329720.0618 | 5796906.5792 | 6339283.6768 | 6199636.4515 | 6137390.4038 | 6039759.2997 | 6578075.4012 | 7231916.6265 | 7805029.2317 | 8551105.2609 | 9288340.8959 | 9994730.9369 | 10926172.2355 | 11789094.5164 | 12593607.0376 | 13521454.1614 | 14574371.2875 | 15540641.0811 | 16596015.8778 | 17613528.7795 | 18605991.6249 | 19459357.5512 | 20370726.3635
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 60340.2637 | Losses (MWh) | 5484.6 | 5526.2113 | 5567.8227 | 5609.434 | 5651.0454 | 5692.6567 | 5734.2681 | 6562.8446 | 6997.6638 | 7438.4431 | 7491.0223 | 7549.1231 | 7607.2239 | 7665.3247 | 7723.4255 | 7781.5263 | 7839.6271 | 7897.7279 | 7955.8287 | 8013.9294 | 8072.0302 | 8130.131 | 8188.2318 | 8246.3326 | 8304.4334 | 8362.5342 | 8421.7525
| 3043834.6939 | Losses ($) | 219384 | 226574.6652 | 233987.7486 | 241629.8771 | 249507.8696 | 257628.7431 | 265999.7179 | 312046.3959 | 341038.9562 | 371583.8445 | 383565.6751 | 396204.148 | 409234.816 | 422669.3898 | 436519.9205 | 450798.8094 | 465518.8178 | 480693.0774 | 496335.1007 | 512458.7919 | 529078.4583 | 546208.8213 | 563865.0284 | 582062.6653 | 600817.7685 | 620146.8376 | 640151.7921
N-1 | 1008.9296 | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 | 100.1707 | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 | 73.3366 | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 | 1.4722 | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 | 315.9581 | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-1 | 75415.3058 | Flex-1 | 3922.9784 | 5310.8216 | 6698.6649 | 8086.5082 | 9474.3515 | 10862.1948 | 12250.038 | 10979.2174 | 9708.3967 | 7539.8422 | 8773.7418 | 7381.6473 | 7586.0302 | 7790.413 | 7994.7959 | 8199.1788 | 8403.5616 | 8607.9445 | 8812.3274 | 9016.7102 | 9221.0931 | 9425.476 | 9629.8588 | 9834.2417 | 10038.6246 | 10243.0075 | 10844.8111
N-1 | 1272587.0328 | Flex-2-1 | 135760.7298 | 136381.6052 | 136667.1611 | 136953.3806 | 137247.061 | 137582.2863 | 137906.4754 | 137693.9567 | 137476.0239 | 137254.5669 | 137608.2964 | 137958.5392 | 138308.9043 | 138647.1577 | 138983.6294 | 139312.8198 | 139636.0492 | 139919.7828 | 140191.7452 | 140456.5237 | 140712.712 | 140921.7634 | 141121.5858 | 141309.7778 | 141490.8863 | 141618.1445 | 141728.4172
N-1 | 526663.8571 | Flex-2-2 | 45808.4214 | 48737.9511 | 50182.2097 | 51691.2111 | 53310.9675 | 55169.0313 | 57028.8184 | 55797.1037 | 54578.426 | 53352.6808 | 55313.5827 | 57337.6933 | 59456.6336 | 61542.8136 | 63663.5828 | 65847.7387 | 68109.8281 | 70213.9163 | 72345.4015 | 74506.0026 | 76709.2379 | 78584.5378 | 80408.9696 | 82173.4363 | 83916.0273 | 85162.031 | 86278.2324
N-0 | 3662.4319 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 | 603.3371 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 | 54.0898 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 | 2.9079 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 | 81.9765 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 355030.5479 | 1354.9655 | 3468.8297 | 5582.694 | 7696.5582 | 9810.4224 | 11924.2866 | 14038.1508 | 12087.1452 | 10461.5877 | 8610.5229 | 12532.4529 | 19218.8075 | 25905.162 | 32591.5165 | 39277.8711 | 45964.2256 | 52650.5801 | 81297.3831 | 109944.1861 | 138590.9891 | 167237.792 | 195884.595 | 242156.0727 | 288427.5504 | 334699.0281 | 380970.5058 | 427241.9834
Commerical(N-1) | EENS | 1473194.2274 | 5622.4102 | 14393.8598 | 23165.3095 | 31936.7591 | 40708.2087 | 49479.6583 | 58251.108 | 50155.4378 | 43410.21 | 35729.2429 | 52003.2359 | 79748.1693 | 107493.1026 | 135238.036 | 162982.9694 | 190727.9028 | 218472.8361 | 337342.3391 | 456211.8421 | 575081.3451 | 693950.8481 | 812820.3511 | 1004823.1921 | 1196826.033 | 1388828.8739 | 1580831.7149 | 1772834.5558
Aggregate | EENS | 1828224.7753 | 6977.3757 | 17862.6896 | 28748.0034 | 39633.3173 | 50518.6311 | 61403.9449 | 72289.2588 | 62242.583 | 53871.7977 | 44339.7658 | 64535.6888 | 98966.9767 | 133398.2646 | 167829.5525 | 202260.8405 | 236692.1284 | 271123.4163 | 418639.7222 | 566156.0282 | 713672.3342 | 861188.6402 | 1008704.9462 | 1246979.2648 | 1485253.5834 | 1723527.902 | 1961802.2206 | 2200076.5392
Residential (N-0) | EENS | 24322736.8672 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6874181.4867 | 7999576.6637 | 9754283.3841 | 11535617.9768 | 13419029.1341 | 15550241.4986 | 17751814.2569 | 19753092.1535 | 21673528.3995
Commerical(N-0) | EENS | 111616614.0139 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29703520.6897 | 34774447.0761 | 42273498.7453 | 50410415.488 | 59093268.8551 | 69213486.1587 | 79553492.0931 | 89158920.0625 | 98364469.7349
Aggregate | EENS | 135939350.8811 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36577702.1764 | 42774023.7398 | 52027782.1294 | 61946033.4648 | 72512297.9892 | 84763727.6573 | 97305306.35 | 108912012.2159 | 120037998.1344
Residential (N-1) | Value for Flex-1 | 382180769.0066 | 15864499.0795 | 22013851.5198 | 28460756.2702 | 35216247.6009 | 42291725.5255 | 49698967.1916 | 57450138.6125 | 52777509.5829 | 47835342.7653 | 38079171.7768 | 45418621.9709 | 39167536.831 | 41258306.7903 | 43429135.5371 | 45682719.2795 | 48021838.9993 | 50449363.0056 | 52968249.5627 | 55581549.5959 | 58292409.4747 | 61104073.879 | 64019888.7476 | 67043304.3134 | 70177878.2271 | 73427278.7712 | 76795288.1687 | 83339893.5939
Commerical(N-1) | Value for Flex-1 | 1574444322.4083 | 65355906.2337 | 90688978.4898 | 117247856.9173 | 145077998.6547 | 174226367.5683 | 204741481.1785 | 236673458.9894 | 217423944.5111 | 197064033.3971 | 156872194.1761 | 187108031.8343 | 161355858.2411 | 169969062.1459 | 178912078.8346 | 188196015.6938 | 197832329.3467 | 207832836.1725 | 218209723.1338 | 228975558.9204 | 240143305.4195 | 251726329.5192 | 263738415.258 | 276193776.3277 | 289107068.9415 | 302493405.0757 | 316368366.0985 | 343329735.4028
Aggregate | Value for Flex-1 | 1956625091.4149 | 81220405.3131 | 112702830.0096 | 145708613.1875 | 180294246.2556 | 216518093.0938 | 254440448.37 | 294123597.6019 | 270201454.0941 | 244899376.1624 | 194951365.9529 | 232526653.8052 | 200523395.0721 | 211227368.9362 | 222341214.3717 | 233878734.9733 | 245854168.3461 | 258282199.1781 | 271177972.6965 | 284557108.5163 | 298435714.8942 | 312830403.3982 | 327758304.0056 | 343237080.6412 | 359284947.1685 | 375920683.8469 | 393163654.2672 | 426669628.9967
Residential (N-1) | Value for Flex-2 | 53475109.1161 | 4633243.5483 | 4770793.6071 | 4900302.2687 | 5033329.0004 | 5170225.4428 | 5312425.0351 | 5458066.4273 | 5585896.7397 | 5716482.1477 | 5849955.4389 | 6011657.6118 | 6177632.5424 | 6348154.5444 | 6522771.8228 | 6702066.4532 | 6885889.1829 | 7074412.2592 | 7266006.7941 | 7462132.993 | 7663132.3015 | 7869037.3536 | 8077746.2768 | 8291430.2625 | 8510049.4399 | 8733980.1779 | 8960381.4919 | 9191542.5672
Commerical(N-1) | Value for Flex-2 | 241047180.1194 | 20885049.3358 | 21505077.1273 | 22088857.0988 | 22688495.306 | 23305576.8221 | 23946563.0922 | 24603063.7983 | 25179278.3558 | 25767911.9255 | 26369563.0674 | 27098460.1831 | 27846617.4034 | 28615271.2387 | 29402385.1553 | 30210582.9461 | 31039191.8333 | 31888988.2462 | 32752629.7263 | 33636698.3698 | 34542733.2959 | 35470881.606 | 36411668.7916 | 37374881.8276 | 38360340.9897 | 39369742.8188 | 40390281.1442 | 41432274.8172
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 294522289.2355 | 25518292.8842 | 26275870.7344 | 26989159.3675 | 27721824.3065 | 28475802.265 | 29258988.1274 | 30061130.2256 | 30765175.0955 | 31484394.0733 | 32219518.5064 | 33110117.795 | 34024249.9458 | 34963425.7831 | 35925156.9781 | 36912649.3993 | 37925081.0163 | 38963400.5054 | 40018636.5205 | 41098831.3627 | 42205865.5974 | 43339918.9596 | 44489415.0684 | 45666312.0901 | 46870390.4295 | 48103722.9967 | 49350662.6362 | 50623817.3844
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 175851094.6125 | 12311267.3461 | 13409297.589 | 14134718.1318 | 14916869.3938 | 15731542.5257 | 16634785.544 | 17527795.189 | 17700803.1928 | 17736497.1808 | 17813893.3966 | 18889864.9578 | 19937712.1496 | 21185354.6635 | 22374288.6742 | 23734941.6325 | 24995759.0206 | 26226140.5593 | 27630716.8564 | 29179870.5135 | 30782900.5504 | 32262754.1843 | 33802002.2581 | 35475056.3796 | 36996533.5236 | 38655870.699 | 40176813.4636 | 41572424.9694
Aggregate ($M) |  | 2564.7661 | 120120600.8638 | 155085922.6375 | 190794554.5265 | 228253763.3107 | 267427691.2751 | 307005423.2952 | 350895755.735 | 326490012.7853 | 300702571.9612 | 252709464.7908 | 292164156.3936 | 265324935.2798 | 281347546.509 | 296404718.2667 | 311540142.4258 | 330077078.2203 | 349915699.8457 | 369108771.3544 | 391979668.5973 | 414912177.1161 | 441322047.3117 | 469004459.743 | 498137726.3648 | 529400852.3623 | 561709111.7946 | 593564944.8035 | 641103946.0242
Aggregate ($M)+ Monetized Losses |  | 2567.8099 | 120339984.8638 | 155312497.3027 | 191028542.2751 | 228495393.1878 | 267677199.1447 | 307263052.0383 | 351161755.4529 | 326802059.1812 | 301043610.9174 | 253081048.6353 | 292547722.0686 | 265721139.4277 | 281756781.325 | 296827387.6564 | 311976662.3463 | 330527877.0297 | 350381218.6635 | 369589464.4318 | 392476003.6979 | 415424635.908 | 441851125.77 | 469550668.5644 | 498701591.3932 | 529982915.0277 | 562309929.563 | 594185091.641 | 641744097.8164
Project Cost |  | 504
Benefit-Cost Ratio |  | 5.0949
Market Participation Revenue (All costs are $x1,000) |  |  | 2048: 482.9875

## Valley South to Valley North
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Baseline | Losses (MWh) | 49667 | 50103.7904 | 50540.5808 | 50977.3712 | 51414.1615 | 51850.9519 | 52287.7423 | 51698.1846 | 51988.3538 | 52278.5231 | 52568.6923 | 52858.8615 | 53149.0308 | 53439.2 | 53729.3692 | 54019.5385 | 54309.7077 | 54599.8769 | 54890.0462 | 55180.2154 | 55470.3846 | 55760.5538 | 56050.7231 | 56340.8923 | 56631.0615 | 56921.2308 | 57211.4
N-1 |  | EENS | 10 | 20.5 | 29.88 | 39.26 | 48.64 | 58.02 | 67.4 | 57.6 | 49.8 | 41.5 | 53.7 | 75.0667 | 96.4333 | 117.8 | 139.1667 | 160.5333 | 181.9 | 244.23 | 306.56 | 368.89 | 431.22 | 453.7 | 524 | 594.3 | 664.6 | 734.9 | 805.2
N-1 |  | IP | 2 | 3 | 4.68 | 6.36 | 8.04 | 9.72 | 11.4 | 10.2 | 8.6 | 6.8 | 9.6 | 11.3333 | 13.0667 | 14.8 | 16.5333 | 18.2667 | 20 | 21.86 | 23.72 | 25.58 | 27.44 | 29.3 | 30.48 | 31.66 | 32.84 | 34.02 | 35.2
N-1 |  | SAIDI | 0.084812 | 0.24283 | 0.34046 | 0.43809 | 0.53572 | 0.63335 | 0.73098 | 0.61765 | 0.52958 | 0.48185 | 0.56681 | 0.9698 | 1.3728 | 1.7758 | 2.1788 | 2.5818 | 2.9848 | 21.0705 | 39.1563 | 57.242 | 75.3277 | 93.4135 | 81.0622 | 68.7109 | 56.3597 | 44.0084 | 31.6571
N-1 |  | SAIFI | 0.006058 | 0.017772 | 0.025047 | 0.032322 | 0.039597 | 0.046872 | 0.054147 | 0.045717 | 0.038992 | 0.031793 | 0.042213 | 0.059766 | 0.07732 | 0.094874 | 0.11243 | 0.12998 | 0.14754 | 0.40051 | 0.65349 | 0.90646 | 1.1594 | 1.4124 | 1.271 | 1.1296 | 0.98824 | 0.84685 | 0.70546
N-1 |  | PFD | 14 | 21 | 23.2 | 25.4 | 27.6 | 29.8 | 32 | 30 | 29 | 29 | 29 | 32.6667 | 36.3333 | 40 | 43.6667 | 47.3333 | 51 | 56.6 | 62.2 | 67.8 | 73.4 | 79 | 82 | 85 | 88 | 91 | 94
N-0 |  | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1121.76 | 1312.64 | 1503.52 | 1694.4 | 1887.4 | 2080.4 | 2273.4 | 2466.4 | 2659.4
N-0 |  | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 136.2 | 145.8 | 155.4 | 165 | 171.84 | 178.68 | 185.52 | 192.36 | 199.2
N-0 |  | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8069 | 12.3278 | 12.8486 | 13.3695 | 31.0249 | 48.6802 | 66.3356 | 83.9909 | 101.6463
N-0 |  | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61663 | 0.54048 | 0.46433 | 0.38818 | 0.85998 | 1.3318 | 1.8036 | 2.2754 | 2.7472
N-0 |  | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 20 | 23 | 26 | 29 | 30.6 | 32.2 | 33.8 | 35.4 | 37
N-1 |  | Deficit Flex-1 | 5445.8257 | 7241.2936 | 9036.7614 | 10832.2293 | 12627.6972 | 14423.1651 | 16218.633 | 15620.1437 | 15021.6544 | 13525.4311 | 14423.1651 | 16913.233 | 17831.3692 | 18749.5055 | 19667.6418 | 20585.7781 | 21503.9144 | 22422.0507 | 23340.187 | 24258.3233 | 25176.4595 | 26094.5958 | 27012.7321 | 27930.8684 | 28849.0047 | 29767.141 | 30685.2773
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 57814.1638 | 62191.7469 | 64361.1052 | 66628.501 | 69068.2267 | 71918.961 | 74820.6792 | 72899.2823 | 71006.3526 | 69131.6161 | 72143.765 | 75301.9259 | 78629.6275 | 81951.0576 | 85383.4246 | 88945.9711 | 92676.8959 | 96145.7299 | 99700.8582 | 103340.2098 | 107065.5182 | 110237.6439 | 113355.671 | 116394.7984 | 119393.946 | 121552.795 | 123501.3671
|  | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| Valley South to Valley North | Losses (MWh) | 49328.2 | 49736.2913 | 50144.3827 | 50552.474 | 50960.5654 | 51368.6567 | 51776.7481 | 51089 | 50877.45 | 50664.2 | 51004.825 | 51341.9516 | 51679.0781 | 52016.2047 | 52353.3312 | 52690.4578 | 53027.5844 | 53364.7109 | 53701.8375 | 54038.9641 | 54376.0906 | 54713.2172 | 55050.3437 | 55387.4703 | 55724.5969 | 56061.7234 | 56398.85
N-1 |  | EENS | 5.8 | 14.4833 | 23.1667 | 31.85 | 40.5333 | 49.2167 | 57.9 | 52.5 | 44.1 | 35.9 | 48.5 | 61.1 | 82.38 | 103.66 | 124.94 | 146.22 | 167.5 | 220.02 | 272.54 | 325.06 | 377.58 | 430.1 | 490.7 | 551.3 | 611.9 | 672.5 | 733.1
N-1 |  | IP | 3 | 4.9167 | 6.8333 | 8.75 | 10.6667 | 12.5833 | 14.5 | 13.5 | 11.8 | 10.1 | 12.9 | 15.1 | 17.26 | 19.42 | 21.58 | 23.74 | 25.9 | 27.82 | 29.74 | 31.66 | 33.58 | 35.5 | 36.58 | 37.66 | 38.74 | 39.82 | 40.9
N-1 |  | SAIDI | 0.015894 | 0.083764 | 0.15163 | 0.2195 | 0.28737 | 0.35524 | 0.42311 | 0.33569 | 0.28198 | 0.19676 | 0.31012 | 0.4465 | 0.87624 | 1.306 | 1.7357 | 2.1655 | 2.5952 | 4.3788 | 6.1623 | 7.9458 | 9.7293 | 11.5128 | 14.8115 | 18.1102 | 21.4089 | 24.7076 | 28.0063
N-1 |  | SAIFI | 0.005298 | 0.01323 | 0.021162 | 0.029094 | 0.037025 | 0.044957 | 0.052889 | 0.047956 | 0.040283 | 0.032793 | 0.044303 | 0.055812 | 0.075253 | 0.094694 | 0.11414 | 0.13358 | 0.15302 | 0.20155 | 0.25009 | 0.29862 | 0.34715 | 0.39569 | 0.45221 | 0.50874 | 0.56527 | 0.62179 | 0.67832
N-1 |  | PFD | 3 | 3.8333 | 4.6667 | 5.5 | 6.3333 | 7.1667 | 8 | 7 | 7 | 6 | 7 | 8 | 9.8 | 11.6 | 13.4 | 15.2 | 17 | 19.6 | 22.2 | 24.8 | 27.4 | 30 | 32.8 | 35.6 | 38.4 | 41.2 | 44
N-1 |  | Deficit Flex-1 | 3808.3607 | 5063.9626 | 6319.5645 | 7575.1665 | 8830.7684 | 10086.3703 | 11341.9723 | 10868.4556 | 10394.9389 | 9921.4223 | 10158.1806 | 11732.4477 | 12452.8192 | 13173.1908 | 13893.5623 | 14613.9339 | 15334.3054 | 16054.677 | 16775.0485 | 17495.4201 | 18215.7916 | 18936.1632 | 19656.5347 | 20376.9063 | 21097.2778 | 21817.6494 | 22538.0209
N-1 |  | Deficit Flex-2-1 | 192864.6662 | 195239.242 | 196366.7654 | 197525.3756 | 198743.9239 | 200140.9384 | 201537.7103 | 200616.8949 | 199696.1493 | 198775.2332 | 200250.3349 | 201766.1655 | 203325.9628 | 204856.9602 | 206421.1883 | 208013.705 | 209643.372 | 211125.2902 | 212613.8546 | 214101.9077 | 215599.504 | 216849.1482 | 218069.3109 | 219248.7447 | 220395.7998 | 221214.4676 | 221946.054
N-1 |  | Deficit Flex-2-2 | 15863.8465 | 17648.2938 | 18532.2445 | 19475.1482 | 20493.6788 | 21703.1962 | 22945.9872 | 22121.1674 | 21313.2168 | 20520.3431 | 21799.1819 | 23155.1608 | 24606.2129 | 26062.5347 | 27614.3526 | 29256.497 | 30979.0521 | 32583.3718 | 34238.6898 | 35926.361 | 37681.7452 | 39178.6708 | 40662.7614 | 42131.1117 | 43588.0399 | 44646.03 | 45597.0962
N-0 |  | EENS(Valley South) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-0 |  | EENS(Valley North) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 31.9333 | 62.8667 | 93.8 | 225 | 356.2 | 487.4 | 618.6 | 749.8
N-0 |  | IP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17.0667 | 33.1333 | 49.2 | 79.68 | 110.16 | 140.64 | 171.12 | 201.6
N-0 |  | SAIDI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0001 | 0.23539 | 0.47069 | 0.70598 | 4.1389 | 7.5718 | 11.0047 | 14.4377 | 17.8706
N-0 |  | SAIFI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0001 | 0.039288 | 0.078476 | 0.11766 | 0.28224 | 0.44682 | 0.6114 | 0.77598 | 0.94056
N-0 |  | PFD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.6667 | 4.3333 | 6 | 8.6 | 11.2 | 13.8 | 16.4 | 19
N-0 Monetized | Residential | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13378.6853 | 184613.5432 | 655744.9507 | 1176150.7446 | 1859058.0492 | 2929109.3858 | 3949158.618 | 5053459.3236 | 6408936.1762
N-0 Monetized | Commercial | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80036.6547 | 1104432.1645 | 3740697.1497 | 6181651.0287 | 8806685.1831 | 13335315.4909 | 17196082.6785 | 21988181.2479 | 28116925.8054
N-1 Monetized | Residential | $ | 1269.4985 | 3507.3999 | 5745.3013 | 7983.2026 | 10221.104 | 12459.0054 | 14696.9068 | 13659.3661 | 11760.7142 | 9813.2626 | 13588.9086 | 17547.2036 | 24911.6828 | 32276.162 | 39640.6412 | 47005.1204 | 54369.5996 | 77256.7859 | 100143.9722 | 123031.1586 | 145918.3449 | 168805.5312 | 204593.5776 | 240381.624 | 276169.6704 | 311957.7168 | 347745.7632
N-1 Monetized | Commercial | $ | 5267.7659 | 14553.906 | 23840.0461 | 33126.1863 | 42412.3264 | 51698.4665 | 60984.6067 | 56679.3462 | 48800.9171 | 40719.9943 | 56386.9837 | 72811.8726 | 103370.6747 | 133929.4768 | 164488.2789 | 195047.081 | 225605.8831 | 320575.9384 | 415545.9936 | 510516.0489 | 605486.1042 | 700456.1595 | 848958.1509 | 997460.1423 | 1145962.1336 | 1294464.125 | 1442966.1164
Flex-2-2 Monetized | Aggregate of Customer and Residential | $ | 4851883.8074 | 5548866.4784 | 5954619.7491 | 6363793.1776 | 6862681.5292 | 7430776.4174 | 7958064.5941 | 7957168.049 | 7874171.1774 | 7776287.7266 | 8450702.8694 | 9080603.7964 | 9916810.716 | 10742147.0818 | 11532452.8263 | 12410650.1702 | 13427370.4397 | 14508754.4423 | 15576671.5917 | 16678510.3769 | 17727086.4233 | 18931202.4562 | 20126360.6731 | 21277070.9728 | 22513024.6587 | 23603677.4869 | 24710377.8006
|  | LMP | 40 | 41 | 42.025 | 43.0756 | 44.1525 | 45.2563 | 46.3877 | 47.5474 | 48.7361 | 49.9545 | 51.2034 | 52.4835 | 53.7956 | 55.1404 | 56.519 | 57.9319 | 59.3802 | 60.8647 | 62.3863 | 63.946 | 65.5447 | 67.1833 | 68.8629 | 70.5844 | 72.349 | 74.1578 | 76.0117
Comparison to Baseline
| NPV of benefit | Component | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048
| 7386.6021 | Losses (MWh) | 338.8 | 367.499 | 396.1981 | 424.8971 | 453.5962 | 482.2952 | 510.9942 | 609.1846 | 1110.9038 | 1614.3231 | 1563.8673 | 1516.91 | 1469.9526 | 1422.9953 | 1376.038 | 1329.0806 | 1282.1233 | 1235.166 | 1188.2087 | 1141.2513 | 1094.294 | 1047.3367 | 1000.3793 | 953.422 | 906.4647 | 859.5073 | 812.55
| 387169.6632 | Losses ($) | 13552 | 15067.4606 | 16650.2242 | 18302.7088 | 20027.4113 | 21826.9097 | 23703.8658 | 28965.1629 | 54141.1386 | 80642.7325 | 80075.2948 | 79612.6936 | 79076.9153 | 78464.5902 | 77772.2257 | 76996.2027 | 76132.7708 | 75178.0448 | 74127.9994 | 72978.4655 | 71725.1249 | 70363.5058 | 68888.9774 | 67296.7455 | 65581.8464 | 63739.1418 | 61763.3134
N-1 | 114.4291 | EENS | 4.2 | 6.0167 | 6.7133 | 7.41 | 8.1067 | 8.8033 | 9.5 | 5.1 | 5.7 | 5.6 | 5.2 | 13.9667 | 14.0533 | 14.14 | 14.2267 | 14.3133 | 14.4 | 24.21 | 34.02 | 43.83 | 53.64 | 23.6 | 33.3 | 43 | 52.7 | 62.4 | 72.1
N-1 | -30.4126 | IP | -1 | -1.9167 | -2.1533 | -2.39 | -2.6267 | -2.8633 | -3.1 | -3.3 | -3.2 | -3.3 | -3.3 | -3.7667 | -4.1933 | -4.62 | -5.0467 | -5.4733 | -5.9 | -5.96 | -6.02 | -6.08 | -6.14 | -6.2 | -6.1 | -6 | -5.9 | -5.8 | -5.7
N-1 | 54.4087 | SAIDI | 0.068918 | 0.15907 | 0.18883 | 0.21859 | 0.24835 | 0.27811 | 0.30787 | 0.28195 | 0.24759 | 0.28509 | 0.25669 | 0.52331 | 0.49656 | 0.4698 | 0.44305 | 0.4163 | 0.38955 | 16.6918 | 32.994 | 49.2962 | 65.5984 | 81.9007 | 66.2507 | 50.6007 | 34.9507 | 19.3008 | 3.6508
N-1 | 0.65104 | SAIFI | 0.00075996 | 0.0045419 | 0.0038851 | 0.0032282 | 0.0025714 | 0.0019146 | 0.0012578 | -0.0022394 | -0.0012916 | -0.0010002 | -0.00209 | 0.0039543 | 0.002067 | 0.00017976 | -0.0017075 | -0.0035948 | -0.005482 | 0.19896 | 0.4034 | 0.60784 | 0.81228 | 1.0167 | 0.81881 | 0.62089 | 0.42298 | 0.22506 | 0.027145
N-1 | 225.5303 | PFD | 11 | 17.1667 | 18.5333 | 19.9 | 21.2667 | 22.6333 | 24 | 23 | 22 | 23 | 22 | 24.6667 | 26.5333 | 28.4 | 30.2667 | 32.1333 | 34 | 37 | 40 | 43 | 46 | 49 | 49.2 | 49.4 | 49.6 | 49.8 | 50
N-1 | 39141.4455 | Flex-1 | 1637.465 | 2177.331 | 2717.1969 | 3257.0628 | 3796.9288 | 4336.7947 | 4876.6607 | 4751.6881 | 4626.7154 | 3604.0089 | 4264.9845 | 5180.7853 | 5378.55 | 5576.3147 | 5774.0795 | 5971.8442 | 6169.609 | 6367.3737 | 6565.1384 | 6762.9032 | 6960.6679 | 7158.4327 | 7356.1974 | 7553.9621 | 7751.7269 | 7949.4916 | 8147.2564
N-1 | 0 | Flex-2-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 | 479183.4057 | Flex-2-2 | 41950.3173 | 44543.4531 | 45828.8607 | 47153.3528 | 48574.548 | 50215.7648 | 51874.692 | 50778.1149 | 49693.1357 | 48611.2731 | 50344.583 | 52146.7651 | 54023.4147 | 55888.5229 | 57769.072 | 59689.4741 | 61697.8438 | 63562.3581 | 65462.1684 | 67413.8488 | 69383.773 | 71058.9731 | 72692.9097 | 74263.6867 | 75805.9061 | 76906.7651 | 77904.2708
N-0 | 3422.1306 | EENS | 22.2 | 65.8 | 102.72 | 139.64 | 176.56 | 213.48 | 250.4 | 216.6 | 182.6 | 151.2 | 202.6 | 292.1667 | 381.7333 | 471.3 | 560.8667 | 650.4333 | 740 | 930.88 | 1120.76 | 1280.7067 | 1440.6533 | 1600.6 | 1662.4 | 1724.2 | 1786 | 1847.8 | 1909.6
N-0 | 527.3168 | IP | 13 | 27 | 34.52 | 42.04 | 49.56 | 57.08 | 64.6 | 59.8 | 52.8 | 46 | 57.4 | 67.3333 | 77.2667 | 87.2 | 97.1333 | 107.0667 | 117 | 126.6 | 135.2 | 128.7333 | 122.2667 | 115.8 | 92.16 | 68.52 | 44.88 | 21.24 | -2.4
N-0 | 49.0833 | SAIDI | 0.047254 | 0.28012 | 0.59718 | 0.91425 | 1.2313 | 1.5484 | 1.8655 | 1.6136 | 1.166 | 0.80459 | 0.56681 | 3.0445 | 4.5886 | 6.1327 | 7.6769 | 9.221 | 10.7651 | 11.286 | 11.8068 | 12.0924 | 12.378 | 12.6636 | 26.886 | 41.1084 | 55.3308 | 69.5533 | 83.7757
N-0 | 2.6068 | SAIFI | 0.023627 | 0.070029 | 0.10932 | 0.14861 | 0.18791 | 0.2272 | 0.26649 | 0.23052 | 0.19434 | 0.16092 | 0.042213 | 0.30678 | 0.39921 | 0.49164 | 0.58407 | 0.6765 | 0.76893 | 0.69278 | 0.61653 | 0.50119 | 0.38585 | 0.27051 | 0.57774 | 0.88496 | 1.1922 | 1.4994 | 1.8066
N-0 | 73.8974 | PFD | 2 | 4 | 4.6 | 5.2 | 5.8 | 6.4 | 7 | 7 | 6 | 5 | 7 | 8.1667 | 9.3333 | 10.5 | 11.6667 | 12.8333 | 14 | 17 | 19 | 20.3333 | 21.6667 | 23 | 22 | 21 | 20 | 19 | 18
Monetized Benefits for Alternative
Residential | Cost of Reliability (N-1) | $/kWh | 4.4933 | 4.6057 | 4.7208 | 4.8388 | 4.9598 | 5.0838 | 5.2109 | 5.3412 | 5.4747 | 5.6115 | 5.7518 | 5.8956 | 6.043 | 6.1941 | 6.349 | 6.5077 | 6.6704 | 6.8371 | 7.0081 | 7.1833 | 7.3628 | 7.5469 | 7.7356 | 7.929 | 8.1272 | 8.3304 | 8.5386
Residential | Cost of Reliability (N-0) | $/kWh | 3.792 | 3.8868 | 3.984 | 4.0836 | 4.1857 | 4.2903 | 4.3976 | 4.5075 | 4.6202 | 4.7357 | 4.8541 | 4.9754 | 5.0998 | 5.2273 | 5.358 | 5.4919 | 5.6292 | 5.77 | 5.9142 | 6.0621 | 6.2136 | 6.369 | 6.5282 | 6.6914 | 6.8587 | 7.0302 | 7.2059
Commerical | Cost of Reliability (N-1) | $/kWh | 166.5977 | 170.7626 | 175.0317 | 179.4075 | 183.8927 | 188.49 | 193.2022 | 198.0323 | 202.9831 | 208.0577 | 213.2591 | 218.5906 | 224.0553 | 229.6567 | 235.3981 | 241.2831 | 247.3152 | 253.4981 | 259.8355 | 266.3314 | 272.9897 | 279.8144 | 286.8098 | 293.98 | 301.3295 | 308.8628 | 316.5843
Commerical | Cost of Reliability (N-0) | $/kWh | 153.8372 | 157.6831 | 161.6252 | 165.6658 | 169.8075 | 174.0527 | 178.404 | 182.8641 | 187.4357 | 192.1216 | 196.9246 | 201.8477 | 206.8939 | 212.0663 | 217.3679 | 222.8021 | 228.3722 | 234.0815 | 239.9335 | 245.9319 | 252.0802 | 258.3822 | 264.8417 | 271.4628 | 278.2493 | 285.2056 | 292.3357
Residential (N-1) | EENS | 34143.207 | 85.4671 | -38.5701 | -162.6073 | -286.6445 | -410.6816 | -534.7188 | -658.756 | -1572.2209 | -1299.1265 | -1202.7397 | -1056.4557 | 1671.6039 | 993.4792 | 315.3545 | -362.7701 | -1040.8948 | -1719.0195 | 4040.5972 | 9800.2139 | 15559.8305 | 21319.4472 | 27079.0638 | 37562.4951 | 48045.9264 | 58529.3577 | 69012.789 | 79496.2203
Commerical(N-1) | EENS | 141676.7537 | 354.6443 | -160.0462 | -674.7367 | -1189.4272 | -1704.1177 | -2218.8082 | -2733.4987 | -6523.9084 | -5390.7071 | -4990.7514 | -4383.7478 | 6936.2967 | 4122.428 | 1308.5592 | -1505.3095 | -4319.1782 | -7133.0469 | 16766.4008 | 40665.8485 | 64565.2962 | 88464.7439 | 112364.1916 | 155865.0412 | 199365.8907 | 242866.7403 | 286367.5899 | 329868.4394
Aggregate | EENS | 175819.9607 | 440.1114 | -198.6163 | -837.344 | -1476.0717 | -2114.7993 | -2753.527 | -3392.2547 | -8096.1293 | -6689.8336 | -6193.4911 | -5440.2035 | 8607.9006 | 5115.9072 | 1623.9138 | -1868.0796 | -5360.073 | -8852.0664 | 20806.998 | 50466.0623 | 80125.1267 | 109784.1911 | 139443.2555 | 193427.5363 | 247411.8171 | 301396.098 | 355380.3788 | 409364.6597
Residential (N-0) | EENS | 22277652.2443 | 160311.262 | 426681.4136 | 622797.584 | 833710.6897 | 1064544.9637 | 1155248.1483 | 1567795.6536 | 1347745.4555 | 1143199.8672 | 1340230.0479 | 1211871.2278 | 1844840.0091 | 2356895.0257 | 2752240.7792 | 3112959.392 | 3866030.0481 | 4800043.3765 | 5605356.4975 | 6860802.8013 | 7814963.1205 | 9098538.4333 | 10359467.2322 | 11559971.0849 | 12621132.1128 | 13802655.6389 | 14699632.8299 | 15264592.2233
Commerical(N-0) | EENS | 102260344.9243 | 903346.6826 | 2253380.2014 | 3310518.2522 | 4447479.3479 | 5587189.7958 | 5454549.1605 | 7543147.8061 | 6412592.3644 | 5385232.8798 | 6340117.1213 | 6361112.919 | 8895771.1264 | 11481103.8359 | 12843987.9109 | 13698596.1883 | 17199347.6609 | 21372792.8101 | 24257449.0613 | 29623484.035 | 33670014.9116 | 38532801.5956 | 44228764.4593 | 50286583.6721 | 55878170.6678 | 62357409.4146 | 67170738.8145 | 70247543.9295
Aggregate | EENS | 124537997.1687 | 1063657.9447 | 2680061.615 | 3933315.8363 | 5281190.0376 | 6651734.7595 | 6609797.3088 | 9110943.4597 | 7760337.8199 | 6528432.747 | 7680347.1692 | 7572984.1467 | 10740611.1355 | 13837998.8616 | 15596228.6901 | 16811555.5803 | 21065377.709 | 26172836.1866 | 29862805.5588 | 36484286.8364 | 41484978.0321 | 47631340.0289 | 54588231.6915 | 61846554.757 | 68499302.7806 | 76160065.0535 | 81870371.6444 | 85512136.1528
Residential (N-1) | Value for Flex-1 | 207361752.6799 | 6621897.889 | 9025240.0833 | 11544610.7011 | 14184309.0748 | 16948776.9855 | 19842603.0985 | 22870527.5316 | 22841542.6096 | 22796814.3618 | 18201663.851 | 22078347.207 | 27489608.933 | 29252436.5342 | 31086224.5099 | 32993419.1115 | 34976544.5529 | 37038205.3794 | 39181088.9069 | 41407967.7324 | 43721702.3186 | 46125243.6543 | 48621635.9928 | 51214019.671 | 53905634.0105 | 56699820.3048 | 59600024.8925 | 62609802.3219
Commerical(N-1) | Value for Flex-1 | 854254218.5995 | 27279785.8511 | 37180672.4982 | 47559553.6114 | 58434140.8601 | 69822732.7501 | 81744232.8966 | 94218168.8424 | 94098761.6153 | 93914497.6713 | 74984166.2182 | 90954677.0199 | 113247086.7709 | 120509288.6742 | 128063821.2434 | 135920762.1357 | 144090510.1843 | 152583795.159 | 161411687.8136 | 170585610.2289 | 180117346.4601 | 190019053.4965 | 200303272.5432 | 210982940.6337 | 222071402.5835 | 233582423.2928 | 245530200.411 | 257929377.3705
Aggregate | Value for Flex-1 | 1061615971.2793 | 33901683.7401 | 46205912.5815 | 59104164.3126 | 72618449.9349 | 86771509.7356 | 101586835.9951 | 117088696.374 | 116940304.2249 | 116711312.0331 | 93185830.0692 | 113033024.2269 | 140736695.704 | 149761725.2085 | 159150045.7534 | 168914181.2472 | 179067054.7372 | 189622000.5384 | 200592776.7205 | 211993577.9613 | 223839048.7787 | 236144297.1508 | 248924908.536 | 262196960.3047 | 275977036.594 | 290282243.5976 | 305130225.3035 | 320539179.6924
Residential (N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commerical(N-1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 1) | Value for Flex-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aggregate of Flex-2 (Component 2) | Value for Flex-2-2 | 158850774.4516 | 11220634.2188 | 12144918.1584 | 12786910.2509 | 13549003.8391 | 14198581.0583 | 15000915.7058 | 15909014.2717 | 15943271.5953 | 15999716.4072 | 16077364.9697 | 17017237.4897 | 18089024.9798 | 19073573.1791 | 20183246.8534 | 21490829.7021 | 22579839.7873 | 23724942.3552 | 24911056.9306 | 26196805.9595 | 27625844.3348 | 29110039.0485 | 30411440.883 | 31944711.5843 | 33332991.3303 | 34748837.6652 | 36032493.5279 | 37232773.5323
Aggregate ($M) |  | 1345.1806 | 46186416.015 | 61030693.7386 | 75823553.0558 | 91447167.7399 | 107619710.7541 | 123194795.4827 | 142105261.8508 | 140635817.5108 | 139232771.3537 | 116937348.717 | 137617805.6599 | 169574939.7199 | 182678413.1563 | 194931145.2106 | 207214698.4501 | 222706912.1605 | 239510927.0138 | 255387446.2078 | 274725136.8195 | 293029996.2724 | 312995460.4193 | 334064024.3659 | 356181654.1822 | 378056742.522 | 401492542.4143 | 423388470.8547 | 443693454.0373
Aggregate ($M)+ Monetized Losses |  | 1345.5677 | 46199968.015 | 61045761.1992 | 75840203.28 | 91465470.4487 | 107639738.1653 | 123216622.3923 | 142128965.7166 | 140664782.6737 | 139286912.4923 | 117017991.4495 | 137697880.9547 | 169654552.4135 | 182757490.0717 | 195009609.8008 | 207292470.6758 | 222783908.3632 | 239587059.7847 | 255462624.2526 | 274799264.8189 | 293102974.7379 | 313067185.5442 | 334134387.8716 | 356250543.1597 | 378124039.2675 | 401558124.2606 | 423452209.9965 | 443755217.3506
Project Cost |  | 185
Benefit-Cost Ratio |  | 7.2733